## Area 100
PRIORITY |  |  |  | UItium #3 Lansing Battery Plant Process Equipment Installation Project OPEN ISSUE TRACKING MATRIX - AREA 100
HIGH |  |  | 1
MED |  |  | 2
LOW |  |  | 3
CLOSED |  |  | 4 | [9 empty] | AS OF DATE: | 2023-11-14 17:21
NO. | PRIORITY | DATE ADDED | DATE CLOSED | ADDED BY | Company | OEM | Process Equipment | Process Equipment # | Process Equipment Location | OPEN ISSUE | RESOLUTION | DUE DATE | RESPONSIBILITY | COMMENTS
1 | 1 | 2023-09-19 |  | RM | PCE | TSI | Mixing |  | Anode & Cathode | Need cable tray layouts & support details for Mixer MCC Rooms and Mixer Rooms |  | 2023-10-03 | TSI | 09/19/23 - TSI has stated finalize drawings will be provided by the end of the week. 10/30 - To be discussed off-line on schedule udpates. IICC to organize a follow up meeting. Cathode CT layout revision planned, 8 clashes with sprnklers to be solved with IPD. Timing clarify needed by 11/1 (follow up mtg) Questions on 480V 2nd floor, 24" vs 9"...? Put on hold for IPD model update. 2D drawing correct, model being updated to reflect. TSI directed install to "STOP" until clarity is provided. Update from LG needed by Wednesday - 11/8 11/7 - Per Juno (TSI) follow the 2D model, until the 3D is released. Duct work location has not been moved. 3D model will be revised. Juno meeting with LG tomorrow (11/8/23), make the model follow the 2D. 11/13 - Continue to follow 2D drawing as lead, disregard any discrepancies btw 2D and 3D model. 3D model being updated end of Nov with IPD. 11/14 - IPD planning to send today, TSI will go through it
2 | 1 | 2023-09-19 |  | RM | PCE | TSI | Mixing |  | Anode & Cathode | Need BOM of ALL cable tray, strut, rod, etc ordered and timing of when balance of material will arrive onsite |  | 2023-11-16 | TSI | 09/19/23 - Throughout the rest of the week all material for line #1. TSI to share BOM list to Copper Range by EOB today. 10/17 - 11/6 material arrival on site. 10/31/23 - TSI giving an answer tomorrow 11/1. Is it all of Line 1 Anode, or all lines. Update for Cathode side as well. TSI to check (Jason Cosner) 11/7/23 - all lines to purchased locally. Feedback within 24 hours (TSI) - due 11/8/23 11/13 - 11/28 updated delivery date from supplier. Anode 1F - 11/28 (all four lines for each) Cathode 2F - 12/12 Cathode 1F - 12/19 Update 11/15 on delivery dates improvements, what is planned when, potential partial deliveries.
3 | 4 | 2023-09-19 |  | RM | PCE | TSI | Mixing |  | Anode & Cathode | Need cable schematics and cable schedules for EMF |  | 2023-09-22 | TSI | 09/19/23 - TSI to upload to Copper Range by end of the week. Closed 9/26
4.1 | 4 | 2023-09-19 |  | RM | PCE |  | Mixing |  | Anode & Cathode | Need cable schematics and cable schedules for Netzsch Mills |  | 2023-10-03 | Netzch Mills | 09/19/23 - Need to review with LG/Ultium. Need to inquire about team members from Netzsch Mills. For construction cable schematics/schedules need to be loaded accordingly. 9/26: Need Netzch contact. IICC to investigate via UC1 10/3: FOB requested, expected by Friday. 10/10: Can be closed, verified per email with Hyungmook Jung that documents on Copper Range are IFC
5 | 4 | 2023-09-19 |  | RM | PCE | TSI | Mixing |  | Anode & Cathode | Need Field cable schematics and Field cable schedules for ALL Mixers (Anode & Cathode 1-4) |  | 2023-10-23 | TSI | 09/19/23 - Pending complete/certified drawings. TSI to report back by the end of the week. ..... 10/23: Anode schedules received (4 cells), Cathode by 10/23 COB. 10/24 - uploaded to Copper Range today, PCE checking and providing feedback 10/30: Cable Schedule received. Anode 10/23; Cathode 10/24. Schematic timing TBD - Phase 1 uploaded today. 11/6 final transfer schematics. Under review. PCE to update status based on latest transmission. PCE moving forward with last transmission. No revisions planned from TSI. 11/14 - PCE designing to what they have
6 | 4 | 2023-09-19 |  | RM | PCE |  | Mixing |  | Anode & Cathode | Need updated panel/bus schedules for MOD 1-4 |  | 2023-10-16 | PCE | 09/19/23 - Pull latest utility matrix with Don Jana and Superior Electric. IICC/PCE to follow-up with team members. 9/26/23: Need contact from LG to release…? 10/3: Utility Matrix Available 2.2 or 3.0. IPD support needed, request sent to Jangpill Oh. Follow up, nothing received. 10/10 - GM following up, moving file to Copper Range. Need by 10/16, PCE to match schedules to utility matrix.
7 | 4 | 2023-09-19 |  | RM | PCE | TSI | Mixing |  | Anode & Cathode | TSI Mixers - Need Material BOM for crates from Korea - Need detail of what is in the crates, TSI to re-send / clarify location. |  | 2023-10-17 | TSI | 09/19/23 - TSI team members will provide BOM list in english and TSI team members will be checking with PCE all crate deliveries. TSI will provide priority list for all process items. 9/26/23: Available, TSI to upload to CR 9/26 PM. 10/3: TSI to send link 10/10 - Need detail of what is in the crates, TSI to re-send / clarify location. Information on CR available, can close and continue to track as needed.
8 | 4 | 2023-09-19 |  | RM | PCE | TSI | Mixing |  | Anode & Cathode | Need Main Mixer Disconnect Switches & Strut Rack |  | 2023-11-14 | TSI | 9/19/2023 - Will be provided as done at UC2. To follow up next week. Switches not built for US Applications. TSI to revise specification and purchase sames switches at U2. Need on-site by 12/15. TSI to define local source taking into consideration lead times. PCE to support as needed on options. 10/24 - TSI checking, 3-4 week lead time TSI to procure same as UC2, will be procured locally - 2 week lead time. TSI to reconfirm status for delivery of 50Hz system. TSI has not ordered yet, PCE to quote options for local supply. 11/7 - PCE wants official submittal from TSI. Close by 11/14 (Approved, Order in System) - Complete by 11/14. 11/14 - parts arriving December 15th. Siemens parts (same as U2) defined.
9 | 4 | 2023-09-19 |  | RM | PCE | TSI | Mixing |  | Anode & Cathode | Need equipment drawings + remote IO panel locations from TSI |  | 2023-10-06 | TSI | 9/19/2023 - TSI to provide drawings by 09/27/23. Posted to Copper Range for record. Need to provide the IO panel naming on the drawings. 9/26: Line 1 drawings to be uploaded 9/27. 10/3/23: Layout received. PCE to review and comment. 10/10 - Close
10 | 4 | 2023-09-19 |  | RM | PCE | TSI | Mixing |  | Anode & Cathode | Need wire label printer from TSI |  | 2023-11-15 | TSI | 09/19/23 - TSI team members to inquire about the label printer and labels with TSI team at UC2 and will follow up next week. 9/26/23: U2 - TSI proivded printer and labels. TSI to provide further feedback next week. PCE to submit DCR for label approval. TSI to purchase (label machine + lables) and lend it to project team. Need date: mid November - order ASAP, continue to track 11/14 - answer tomorrow 11/15, same label maker as UC2
11 | 4 | 2023-09-19 |  | RM | PCE |  | Mixing |  | Anode & Cathode | Need all Bus plugs for Mixer Equipment |  | Ongoing | Superior | 09/19/23 - Superior Electric has procured the bus plugs at their warehouse. PCE and Superior Electric to coordinate deliveries/logistics of the bus plugs. Need to verify fuses were purchased by Superior Electric. 9/26: SE working on lead times and required plugs, fuses + process to monitor usage through job. 10/3: Plugs purchased and local. PCE will have a connex to store plugs after full moblilization including trailers. Monitor until plugs delivered. Quantities ordered communicated, PCE to compare back to utility matrix and provide feedback. Quntities correct, verify delivery dates and turnover process (PCE).
12 | 4 | 2023-09-19 |  | RM | PCE |  | Mixing |  | Anode & Cathode | Verify Main Mixer Disconnect & Core Drill Locations (we have a recommendation from U2) |  | 2023-10-17 | PCE/TSI | 09/19/23 - PCE to provide what they utilized at UC2. To review with Don Jana and team members to incorporate drawings. 9/26: Core drill locations sent over. Confirmation needed GM/IICC/TSI. 10/3 - Proposal submitted based on UC2, PCE to send drawing and provide feedback. 10/10 - Drawings sent yesterday, TSI to provide feedback. No issues using U2 as base, add to GAD. If agreed, can close
13 | 2 | 2023-09-19 |  | RM | PCE | TSI | Mixing |  | Anode & Cathode | Need all vibration sensors, RPM sensors, temperature sensors going in Main Mixer Motor Enclosure |  | 2023-11-28 | TSI | 09/19/23 - Need to provide list and ETA of parts arriving onsite to PCE. TSI to look into providing complete list and to follow up next week. 9/26: RPM & Temp already installed. Vibration sensors to be installed on-site. To be shipped 10/6, arrival date end of October. 10/23: Still tracking for end of October. Installation manual udated. Check when main mixers delivered (ROS: 11/12). Need to track lose components accordingly. Status of what is on-site, what is in transit - TSI 11/7 - currently slated for 3 weeks from now arrival Review what is on the Main Mixers when they arrive - 11/28.
14 | 2 | 2023-09-19 |  | RM | PCE | TSI | Mixing |  | Anode & Cathode | Need all VC type disconnect switches for all motors not shipped on skids i.e. Ring Blower Motors, Hydraulic Pump motors, Mazzella Rail etc. |  | 2023-12-15 | TSI | 09/19/23 - TSI to review internally to verify all items are coming to site. If not, then these items would potentially need to be purchased local to the site. 9/26: Missing VC type disconnect switches to arrive mid December. 11/7 - switches procured in Korea, and on site December 15th. Confirm Delivery Dates on these items 11/14 - still on track for Dec 15th
15 | 2 | 2023-09-19 |  | RM | PCE | TSI | Mixing |  | Anode & Cathode | Need delivery date for Line 1 MCC Panels |  | 2023-12-15 | TSI | 09/19/23 - TSI has stated that LGENS has requested to modify MCC Panels. MCC Panels will be delayed per TSI to mid-November to ship from Korea. 9/26: Mid December arrival. Need to review schedule impact. 10/3/23: PCE / IICC to review impact on schedule. 10/10 - Continue to monitor schedule, depends on meeting other committments. 11/6: TSI to re-confirm. 11/14: Status? Shipped 11/1, roughly 45 days
16 | 4 | 2023-09-19 |  | RM | PCE | TSI | Mixing |  | Anode & Cathode | Need cable schedule of pre-run main mixer cables |  | 2023-09-26 | TSI | 09/19/23 - TSI to review internally to verify with their team and report back to the team. 9/26: Closed, TSI reporitng no cable to be run.
17 | 2 | 2023-09-19 |  | RM | PCE |  | Mixing |  | Anode & Cathode | Need Limit switches and dustbin high level switches for DC Towers |  | 2023-11-10 | Ghafari | 09/19/23 - Capture accordingly to submit a DCR to Ghafari for review. 9/26: GF aware, meeting on 9/29. Update? 10/10: Roll into Ghafari weekly meeting 10/24 - Meeting, 10/27 will be able to give information to PCE Status:? 11/7 - review Friday 11/10 11/15 DCR review
18 | 4 | 2023-09-19 |  | RM | PCE |  | Mixing |  | Anode & Cathode | Need circuit requirements / equipment layout for IQC Room |  | TBD | PCE | 09/1923 - May want to capture in our bundle of utilities to handle. Provide DCR for clarification. 9/26 - Don to review and advise. 10/10: Roll into Ghafari weekly meeting 10/17 - UC2 baseline to be sent from PCE as a base for discussions with Ghafari. General Requirements for IQC room posted to CR 10/19. PCE to review and provide questions or points for clarification. Feedback to be sent back through IICC DCR process as needed.
19 | 3 | 2023-09-19 |  | RM | PCE | TSI | Mixing |  | Anode & Cathode | PCE needs terminals labeled in the touch panels & all RIO panels to be installed on the 2nd floor on Anode & Cathode (this came up at U2 and just trying to get ahead of it if it becomes and issue on U3) |  | Ongoing | TSI | 09/19/23 - Need panel drawings labled completely from TSI. TSI to review their team members internally and report back to the team. 9/26/23 - Continue to monitor to avoid in future.
20 | 4 | 2023-09-19 |  | JA | IICC | TSI | Mixing |  | Anode & Cathode | Brass Monument Layout for Mixing |  | 2023-10-04 | TSI/IICC | 09/19/23 - R&E will be onsite tomorrow to review layout process. Further review into next week on layout plans. 9/26/23: R&E engaged, brass monuments via R&E planned for next week. Mounting to be discussed with UC2 / BMC 9/27. 10/3: R&E visit complete. Updated drawing. TSI to dimension and approve by 10/4 close of business. TSI to provide back to Korea for approval, latest Friday morning so IICC can re-engage R&I. 10/30 - Final drawings being updated, TSI to clean up dimensions.
21 | 4 | 2023-09-19 |  | JA | IICC | TSI | Mixing |  | Anode & Cathode | Penetrations in Mixing. Need to review and provide drawings. |  | 2023-10-30 | TSI | 09/19/23 - Were all holes cored prior to equipment being set? Need to verify with TSI and provide drawings to crosscheck equipment layouts. 10/3 - Penetration layout available on CR. 10/10: Assess with R&E dimensioned feedback from Brass Datum work this week. 10/17: Will share with general arrangement drawings - General Arrangement Anode - 10/25 First Floor, 10/20 Second Floor General Arrangement Cathode - first & second floor 10/30 10/24 - still on track. GA uploaded yesterday 10/31 - still nothing for piping. Update 11/1 See #35 & #37
22 | 4 | 2023-09-19 |  | JA | IICC | TSI | Mixing |  | Anode & Cathode | Need approval on Mixing Jig |  | 2023-09-22 | TSI | 09/19/23 - IICC to confirm drawings posted to Copper Range are IFC drawings from TSI prior to fabrication. 9/26/23: Complete & Released from TSI
23 | 4 | 2023-09-19 |  | JA | IICC | TSI | Mixing |  | Anode & Cathode | OHT Hoist (2nd floor) Layout needs to be provided |  | 2023-10-17 | LG | 09/19/23 - Need to provide hoist layout to confirm abatement locations. 9/26/23 - Layout for hoist as well as complete area 100. BMC to review locations. 3D models to be provided tomorrow - provide Mazzella contact for site visit. 10/3 - Locations uploaded on CR, clash with fire suppression Feedback requested from TSI. Review off-line for next steps. 10/10 - Need layout from LGES Team. Ultium Jang to follow up with LG Kiju. Next step, BMC to start with fire abatement. Decision on fire abatement outstanding. 10/31 - Scope requested to provide to Skyline. Skyline to visit 11/8. OHT on Copper Range, lines 1 & 2 defined for Skyline. Line 1 2nd Floor Service drawings missing.
24 | 4 | 2023-10-02 |  | Kevin Bartos | BMC | TSI | Sus Plate |  | Anode & Cathode | BMC requesting to adapt the Sus Plate layout to reduce the installation complexity. TSI reporting Line 1 can't be changed, Line 2, 3, 4 can be reviewed accordingly. |  | 2023-10-17 | TSI | 10/6 - Updates possible, BMC proposal challenged by lack of material. Line 1 as TSI provides. Updated drawing by 10/6 on what is possible. 10/10: Expecting TSI response by 10/11. TSI to approve Anode and continue to review Cathode. Material expected not to be an issue. TSI to formally respond to DCR with approval and modified drawing for BMC to follow. Target to move to Cathode 1F by 10/18 latest. Need TSI Approval by 10/16 Feedback from TSI 10/17
26 | 1 | 2023-10-02 |  | Rob Mard | PCE |  |  |  |  | PID Drawings and List of Field Devices identifying which panels they connect to. |  | 2023-11-21 | TSI | 10/3 - PID uploaded, PCE to review. 10/10: Need a list of field devices by skid to be installed by 10/31 Instrument list uploaded on CR. Updated list for Anode uploaded, PCE to review and provide feedback. TSI to provide file path. PCE looking for device numbers to plan term and pull packages. PCE to check ISO's. 10/31 - device list in 3 weeks - 11/21 list 11/7 - TSI had a discussion with PCE regarding what they wans/need
26 | 4 | 2023-10-02 |  | Paul Kurtzhals | Conti |  |  |  |  | Conti requesting to Bring in 6 Pack Welding Machines into each Mixing room and on each Floor. Need 460v/100 Amp for Each. 4 total to Start. Is this power available in Building? |  | 2023-10-06 |  | BMC: Need one week to resolve.
27 | 4 | 2003-10-02 |  | Jason Einsporn | PCE |  |  |  |  | 100-amp power back on each floor , located in the middle placed near or on line 3 out of the way of line 1 and 2 for production . |  | 2023-10-06 |  | What would help is to have panel boards strung from main power packs to the contractors laydown and lift charging areas .
28 | 4 | 2023-10-03 |  | Paul Kurtzhals | Conti |  |  |  |  | TSI Drawing index: Is one available? |  | 2023-10-10 | TSI | Shared 10/5, Conti has provided prioritization.
29 | 1 | 2023-10-03 |  | Paul Kurtzhals | Conti |  |  |  |  | Schedule for Drawing Releases? |  | 2023-11-15 | TSI | Meeting held 10/5. Status: Piping Drawing Release Plan: Support Iso Anode 2F 9/27 9/27 Cathode 2F 10/15 - 10/30 10/15 - 10/30 Anode 1F 10/30 10/20 10/30 - 10/20 Cathode 1F 10/30 - 10/30 10/30 - 10/30 Coater 11/5 11/15 10/31 - all four (4) 10/30 dates still waiting on per Conti Mech. Cathode delivered 11/1. Conti working through the drawings. 11/7: Status Conti? - waiting on specs. Pipe arrangement drawings need measurements and dimensions. Status of all hold drawings (150 cathode, Netzsch Mill). Updated schedule this week - Holding the 16th. Piping Material Specification due 11/15...no date? Discrepanciies on interface with facilities (Ghafari)? Release per the schedule. Status: same, 11/15, separate meeting needed for all parties involved to determine and agree scope. Start with DCR meeting 11am Wed.
30 | 1 | 2023-10-03 |  | Paul Kurtzhals | Conti |  |  |  |  | Hanger layout Drawings for Cathode and Anode Coater Corridors requested. |  | 2023-11-05 | TSI | Need availability date from TSI? Coater - 11/5 - on track (revision status unclear). Corridor ISO released, Hanger's on-hold. Tracking for 11/15 release. 11/7 - considering Brass datums again now in Area 200, answer by Friday 11/10 11/14 - dimensions off the steel per TSI. Meeting separate to discuss brass datums with TSI, answer tomorrow 11/15
31 | 2 | 2023-10-03 |  | Paul Kurtzhals | Conti |  |  |  |  | Schedule for Mixing Equipment arrival? | Schedule for Mixing Equipment arrival? | 2023-11-24 | TSI | FOB shared 10/10. Contractors to advise if there are additional questions on material arrival. A,C MCC Panel,Consle desk - 11/15 FOB Rest shipped on or before 9/30 10/23: Next Deliveries: 11/4, 11/12, 11/19 - TSI to double check. Anode & Cathode? 10/31 - no delivery date changes at this time Confirm delivery dates 1-1 to 1-4. Anode & Cathode Mods 1.1 - 1.4 onsite by 11/24 POR
32 | 4 | 2023-10-05 |  | Rob Mard | PCE |  |  |  |  | Interference air duct going through cable tray location call out |  | 2023-10-17 | UC | IPD has agreed to move the duct work 5 meters. Date: TBD Ultium Jang Lee to follow up on next steps. IPD to relocate by month end.
33 | 4 | 2023-10-05 |  | Jason Einsporn | PCE |  |  |  |  | Anode MCC Roof Fire Sprinkler Schedule - Sprinklers incomplete prior to PCE Start |  | 2023-10-17 | UC | 10/10 - Feedback - no sprinklers planned. Ultium Jang Lee to follow up on next steps.
34 | 4 | 2023-09-29 |  | Paul Kurtzhals | Conti |  |  |  |  | Please provide other means to Access Model. We cannot extract from Copper Range. At U2, TSI created a Google Drive Account and Supplied Username and Password in order to retrieve Model. |  | 2023-10-10 | TSI | 10/9 Status: Juno to create a new Google account for UC3.
35 | 1 | 2023-09-30 |  | Paul Kurtzhals | Conti |  |  |  |  | Please provide means to request openings and their location approval in Pre-Cast Wall Separating Mixing and Coater Room for Both Cathode and Anode: Need to run Piping Through This wall From Mixing to Coaters. Information Requested: 1) Point of Contact (Who Approves the Layout) 2) Pre-cast Layout and individual Slab Drawings 3) Areas in Slabs that are off Limits. 4) Who Cuts the Openings? Wall Penetrations final agreement and release needed. |  | 2023-11-15 | TSI / Ultium | TBC 10/18 @ 2pm meeting with IPD team. 10/17: Use the same as UC2 -->Point person to coordinate various stakeholders up to cutting. Wall penetration locations uploaded to CR. Provide cut zone from IPD, Conti to review and provide feedback. 10/31 - holes will be layout done EOB Thursday. Field verify with TSI? Update locations based on latest info, walk for final agreement. Process defined for BMC penetrations - 11/10. Contractors/OEMs to field mark, IICC Superintendent to submit request to BMC. 11/7 - Layouts being updated (TSI), team to mark off new area (TSI/Conti/IICC/GM), field verify for final approval. Line 1 by Friday 11/10 11/13...Status? TSI has guidance on "no fly zone", TSI to confirm locations by 11/15 Wednesday. Revisions in process for holes & piping. 11/14 - location for Line 1 Anode tomorrow, potential clash per TSI
36 | 2 | 2023-10-10 |  | Rob Mard | PCE |  |  |  |  | Need schematics for AC / DC towers |  | 2023-12-01 | Ghafari | First week of December for supplier decision and schematic availability. Interface meeting btw TSI & Ghafari will be needed. Assumes all AC/DC towers.
| 4 | 2023-10-13 |  | Kevin Bartos | BMC |  |  |  |  | Steel Abatement - Anode/Cathode 1F target to complete soon. |  |  |  | Targeting to decide contractor week of 10/20.
37 | 2 | 2023-10-13 |  | Kevin Bartos | BMC |  |  |  |  | Core Holes - As built core holes have been sent to TSI for approval |  | 2023-11-15 |  | TSI to field verify 11/1 11/7 - Pre-drilled holes sizes - no change 8 inches or less, no change in location TSI approved to proceed TSI to deliver Pan drawings with hole layout --> TSI not providing Pan drawings. Conti / BMC to identify Pan hole locations. Cathode 2F Line 1 Core Locations needed. TSI to provide date...? 11/13 - Two interferences found last week, immediate DCR and resolution. Current status...? Potential to complete Anode by 11/13. Timing for Cathode? Drawings for Cathode Core holes, drip pan drawings for Line 1. 11/14 - Line 1 Anode complete at this time, now looking for Cathode locations. TSI providing Cathode Friday 11/17
| 4 | 2023-10-16 |  | Jason Hills | PCE |  |  |  |  | Need the following panels to be installed complete - 'PDP1A1H-2-4', 'PDP1A1H-2-3', 'PDP1B1H-4-4' Need delivery & install complete date from Superior. Follow up with Tyler. |  | 2023-11-01 | Superior | Feeds for AC/DC towers. 10/17/23 - Discuss with Superior End of December Installation of Panels planned.
38 | 2 | 2023-10-17 |  |  | BMC |  |  |  |  | Need to agree on brass datum locations for Coater Anode/Cathode Corridor/Line 1 locations |  | 2023-11-14 | BMC / TSI | BMC to propose locations based on U2, TSI to approve IICC to work R&E on arranging next visit. DCR submitted, requesting to use round numbers - TSI to approve to bring R&E 10/24 - final checks. 10/31 - Usage not planned by install contractors. Need to check need with FA. FA requesting Brass Datums. Location needed to support FA. Drawing sent to Kiju for review and approval. Check on scope to install. FA team has until Monday 11/13 update / freeze current locations. 11/13 - Proposal received from Kiju. Hyungmook to review with TSI for final confirmation 11/15.
| 4 | 2023-10-23 |  |  | BMC |  |  |  |  | Delivery Status Mixing Equipment - update weekly |  |  |  | Include Mathias Hyungmook has updated material on CR Combine with #31
| 4 | 2023-10-23 |  |  | BMC |  |  |  |  | DCR on perimeter trim preference for Mixing Sus Plate Area |  |  | GM / Ultium | Submitted, sent to BMC for evaluation.
39 | 4 | 2023-10-23 |  |  | BMC |  |  |  |  | DCR #5 on anchors - clarification on standard sizes or metric. |  | Ongoing |  | American anchors to be purchased for Lines 2-4. 10/31 - feedback Friday on our to proceed through the rest. Line 1 to be imperial size Review with Don 11/7. BMC & Don speaking Move forward with Line 1. Remaining TBD at a later date.
| 4 | 2023-10-23 |  |  | Conti |  |  |  |  | NMP Line from SRP - Double wall? Path of travel defined? |  |  | TSI | 10/24/23 - give the piping drawing 10/30 per Juno. Link provided 11/5, team to review. 11/7 - Conti taking a look at it, and may reopen later on
| 4 | 2023-10-23 |  |  | Conti |  |  |  |  | DCR on 2" socket weld tee…? |  |  | TSI | 10/24/23 - verify once more per TSI and will update the drawing. Main airline, stainless, anode second floor. By the end of the week 10/27. Follow up tomorrow 10/25/23 with TSI. Conti to provide quote to IICC for approval (after drawing's submission).
| 4 | 2023-10-30 |  |  | PCE |  |  |  |  | Netzsch Panel relocation, in-line with other panels in mixing. Same as U2 |  |  | LGENS | PCE to submit a DCR to clarify feasiblity (complete) 10/30 - Discuss with Minkoo & LG stakeholders. Approved to follow U2 footprint.
| 4 | 2023-10-30 |  |  | PCE |  |  |  |  | Remote IO Panel Re-location. RIO Panel placement impedes working clearances. |  |  |  | U2 RIO moved to our disconnect racks to avoid. PCE may move disconnect rack to avoid interference. Discuss 11/7 for update.
| 4 |  |  |  | BMC | TSI |  |  |  | Drip Pans interfering with Building Wall. |  | 2023-11-07 | TSI | Can the drip pans be pulled away from the wall and not effect the equipment or does this move effect everything? TSI evaluating the move, revised GAD in process. 10/31 TSI to provide date on updated drawing. 10/31 - Barton Malow to verify drawing. TSI moved pans to avoid clash. Closed.
40 | 4 | 2023-11-07 |  |  | Conti |  |  |  |  | Conti running low on 62mm Strut. Material will run out by 11/10. Comparing what has been ordered vs what has been used. TSI to review atdditional orders in the pipeline |  |  |  | Update 11/8 Order vs. Usage. What else is in the pipeline? Mis-labeled - enough 62mm strut to continue
41 | 2 | 2023-11-07 |  |  | Conti |  |  |  |  | Putting together a list of material that is running low (Reducers) |  | 2023-11-14 | TSI | Update 11/8 11/10 - Complete Air System. Status TSI? TSI evaluating the short and long term shortage. Collecting quotations and will advise on what will be ordered and ETA. Fitting take off of model needed to forecast. Kevin Moon key point of contact for material. 11/14: TSI has a list of what needs to be ordered in the states. Will provide delivery dates (Friday)
42 | 2 | 2023-11-10 |  |  | BMC |  |  |  |  | Area 200 Anode & Cathode Corridor #1 tank layouts needed |  | 2023-11-14 | TSI | Input for Sus Plate planning. General Layout on CR. Exact locations based on Brass Datums. General locations are sufficient. BMC feedback? 11/14 - BMC double checking, will confirm information is there
43 | 2 | 2023-11-10 |  |  | IICC |  |  |  |  | Brass Datums for Lines 2, 3, 4 Anode & Cathode needed |  | 2023-11-15 | TSI/IICC | TSI to propose locations - Proposal expected by 11/15 Wednesday 11/14 - TSI to provide tomorrow, want the centerline double checked again for lines 2-4
44 | 1 | 2023-11-09 |  |  | Conti elec. |  |  |  |  | Jumbo Roll stocker 1 and Input foil are fed from the mixing bus line in Area 100, request to feed from Area 200 bus |  | 2023-11-21 | Ghafari/Dunham | DCR in process to evaluate moving to Area 200 bus. To be presented to Ghafari 11/15
45 | 2 | 2023-11-09 |  |  | Conti elec. |  |  |  |  | Location of the cim plugs for Area 100 - |  | 2023-11-21 | Ghafari/Dunham | Area 100 drawings show no process recepticles, need info on what fed from and which panel. 60 extra recepticles Lesson Learned from UC2.
46 | 4 | 2023-11-09 |  |  | Conti elec. |  |  |  |  | Are the AGV's in mixing RM needed for Sample build? |  | 2023-11-14 |  | AGV's not mandatory for sample build. Per UC1/2 raw material input by cart / manual transport. 11/14 - plan to keep AGV's in schedule, if not ready OEM will have a manual way to use it
47 | 3 | 2023-11-09 |  |  | Conti elec. |  |  |  |  | Layout of AGV's for mixing rooms |  | 2023-11-21 |  | Cointec to provide, Malyk to follow up with Kiju.
48 | 1 | 2023-11-09 |  |  | Conti elec. |  |  |  |  | Raw mixing stocker CAD drawing for layout of main panels Anode and cathode |  | 2023-11-21 | Cowin Tech | Cowin Tech to provide, Malyk to follow up.
49 | 1 | 2023-11-09 |  |  | Conti elec. |  |  |  |  | Install manuals for All FA equipment |  | 2023-11-21 | Cowin Tech | Cowin Tech to provide, Malyk to follow up.
50 | 2 | 2023-11-13 |  |  | PCE |  |  |  |  | Relocate EMF Panel - PCE would like to relocate the EMF panel into the Cell 1 grouping in the MCC rooms |  | 2023-11-21 | TSI | Match UC2 layout, LL. TSI to provide feedback by 11/17. 11/14 - TSI providing feedback Friday
51 | 2 | 2023-11-13 |  |  | PCE |  |  |  |  | Netzsch - Need BOM of items shipped and total ordered for Line 1 |  | 2023-11-21 | IICC | IICC to contact Netzsch for support.
52 | 2 | 2023-11-13 |  |  | BMC |  |  |  |  | Service Rail Drawings 2nd floor needed. Owner? SIO hopper air hoist |  | 2023-11-21 | GM Quincy | Check with FA Team on scope. 11/14 - potential clash per BMC (Kevin Bartos), OHT & Service Rail share column. Getting together offline to further discuss matter within the next 24 hours
1
2
3
4

## Area 200
PRIORITY |  |  |  | UItium #3 Lansing Battery Plant Process Equipment Installation Project OPEN ISSUE TRACKING MATRIX - AREA 200
HIGH |  |  | 1
MED |  |  | 2
LOW |  |  | 3
CLOSED |  |  | 4 | [9 empty] | AS OF DATE: | 2023-11-14 17:21
NO. | PRIORITY | DATE ADDED | DATE CLOSED | ADDED BY | Company | OEM | Process Equipment | Process Equipment # | Process Equipment Location | OPEN ISSUE | RESOLUTION | DUE DATE | RESPONSIBILITY | COMMENTS
1 | 2 | 2023-10-02 |  | Paul Kurtzhals | Conti | TSI |  |  |  | Hanger layout Drawings for Cathode and Anode Coater Corridors requested. |  | 2023-11-15 | TSI | Support 11/5; Iso 11/15
| 4 | 2023-10-16 |  | Brian Klapp | IICC | Daejin |  |  |  | Floor SUS Plate coordination - Pre-cut material from Korea needs to be reviewed for installation and final layout. Raw Material Tank Bottom Reinforcement Plate Corridor wall (errors between actual measurement and installation dimensions due to non-installation) Fuel piping support (post installation position) |  | 2023-10-25 | BMC | Need a stakeholder review to determine next steps (IICC/BMC/Daejin) Agree on a plan to start. Drawings by Friday 10/20 from Daejin Need to distribute to BMC & IICC for review. Discussed with Daejin, issue closed by Daejin.
2 | 2 | 2023-10-16 |  | Brian Klapp | IICC | Daejin |  |  |  | Corridor Sus-Plate drawings needed. |  | 2023-11-15 | Daejin | BMC to review 10/24: Coordination meeting held with Daejin. Layout, Sequence, Scope discussed. Questions to be submitted via DCR. Schedule & Scope concerns based on Daejin design. 10/30: Clarification on-going on material order status. Team to discuss approach for pit walls and work sequence with Norris Bros. 10/31/23 - BMC is starting, and Daejin going out today. Starting point has been established. Need modification around the column due to grouting Desired sequence & material availability established. See meeting minutes. Pit wall layout (which wall?) to be confirmed Thursday. Pit cost and timing for one piece option to be reviewed Thursday. --> Stay with Daejin design Layout update to be shared with team - IICC to confim. TSI to work on tank layout out, Conti to work on panel layout in corridor
| 4 | 2023-10-16 |  | Brian Klapp | IICC | Daejin |  |  |  | Anode Line 1 centerlines shot, 6" offset to drawing due to pits being referenced to OD of column vs. center. Daejin to provide drawings to modify platforms for top coater pit layout. |  | Ongoing | Daejin | Lines 1-4 Anode top needed. Pits off by 6 inches on the Anode side - due 10/20 All requirements captured & approved? Confirm final drawings released. 10/31/23 - new drawing to be released Friday 11/3 11/7 - Date for line marking for Cathode Line 1...?
3 | 2 | 2023-10-16 |  | Brian Klapp | IICC | Daejin |  |  |  | Centerlines for Cathode Line 1 needed, confirm alignment and or additional measures to be taken. |  | 2023-11-14 | Daejin / Norris | See meeting minutes. Approved to proceed and continue layout based on columns NOT pit center line. 11/7 - Date for line marking for Cathode Line 1...?. 11/7 - Cathode complete Line 1. 40mm interfernce with the building column. Same as Anode. Updated layout dimensions 11/17 Cathode offset of 40mm same as Anode. Interference with building column. Update 11/14. Impact on pit platform (20mm) and see if any further input for approval. 11/14 - Jangpill, and construction team to review this further. GM, IPD, Sail team, and LG construction for this discussion
4 | 2 | 2023-10-16 |  | Brian Klapp | IICC | Joong Wong |  |  |  | Damaged crates from Joong Wong - |  | 2023-11-15 | Joong Wong | Short and Long term corrective measure needed. Joong Wong re-crating all incoming material, will add 3 weeks to delivery dates. Impact to be confirmed. Team requesting earlier ship dates (-3 weeks) to mitigate. 10/31/23 - line 1 to be repacked, lines 2-4 will be better packaged before shipping. GM Daggy involved in timing impact. Continue to monitor. YK asking for expediting of material re-pack and shipment. Team to determine what critical parts are stuck in re-pack. Impact on Anode / Cathode timing to be determined. YK to communicate delivery dates on re-pack crates 11/15
5 | 2 | 2023-10-16 |  | Brian Klapp | IICC | Joong Wong |  |  |  | Complete duct work installation ahead of Coater bridge installation |  | Ongoing | IICC | Duct work contractor decision pending, determine start date to stay ahead of Norris per Coater Schedule. Targeting to mobilize Norris starting next week. Norris bros will mobolize and get them kicked off. Steel will start going up 10-30-23 Contractor identified, planning discussions in process. Site visit planned for 11/2. Drawings communicated. Trades Meeting 11/9. Allied to schedule work for Anode 1 next 1-2 weeks. AMS site visit 11/10. Mobilizing team week of 11/13.
| 4 | 2023-10-16 |  | Minkoo | LGES | Daejin |  |  |  | Oven staging start date |  | 2023-10-17 | IICC | 12/4 start date for Hirano. TBC. 10/17/23 - start dates and completion dates for the ovens and structure
6 | 2 | 2023-10-16 |  | Brian Klapp | IICC | Daejin |  |  |  | Delivery dates for Coater machines needed |  | Ongoing | Daejin | Dryers & Ovens planned for early November. Winders on-site. Panels 12/1 Coaters departed Japan 10/25 - ROS to be confirmed. Target ROS 12/20
7 | 2 | 2023-10-16 |  | Brian Klapp | IICC | IPD |  |  |  | Room Readiness Dates - |  | 2023-11-07 | BMC | Cathode Ovens Line 1 - 10/23 Top and Back 11/7 Daejin communicated Back as a priority for reference Status? 10/31/23 - back on cathode pushed to 11/17. Back Coater Anode moved to 11/9. Line walk 11/7 to review include space to set ovens. John requested more detail from BMC. Update this week on co-hab 11/14 - room ready dates 11/17
8 | 2 | 2023-10-16 |  | Walt Phillips | Conti | Hirano |  |  |  | Documentation Requested (DCR1): Bus layout drawings dimensioned PDP Locations dimensioned Bus Installation schedule PDP installation dates Electrical IFC drawings |  | 2023-10-31 | IICC | Follow up next week with Superior, Conti, PCE
9 | 2 |  |  | Brian Klapp | IICC |  |  |  |  | 200 mm shift in Anode Coaters - What is impact on mechancial and electrical layouts…? |  | Ongoing |  | Continue to track as layouts for other systems are defined.
10 | 3 | 2023-10-17 |  |  | BMC |  |  |  |  | Need to agree on brass datum locations for Coater Anode/Cathode Corridor/Line 1 locations |  | 2023-11-14 | BMC / TSI | BMC to propose locations based on U2, TSI to approve IICC to work R&E on arranging next visit. DCR submitted, requesting to use round numbers - TSI to approve to bring R&E 10/24 - final checks 10/30 - Datum's for corridors cancelled, not needed across contractors. Check if required for FA FA Requesting Brass Datums, need to define an optimal location. Stakeholder meeting needed. Kiju is identifying locations, provide feedback specific to FA. Confirm if new locations needed or use existing - Hyungmook Kiju submitted proposal. Final agreement with TSI input needed. Hyungmook.
| 4 | 2023-10-30 |  | LG | Joong Wong |  |  |  |  | Review layout and provide plan to adjust for ~40mm shift in duct work (Due: 10/31) |  | 2023-10-31 | Joong Wong | 10/31/23 - need official email JW ok to accommodate shift.
11 | 2 | 2023-10-30 |  | GM | Norris Bros |  |  |  |  | Coater Top Wall Opening Drilling (Cathode and Anode 2,3,4 line) + 2nd floor - when are the cutouts required? |  | 2023-11-07 | IICC | 2nd floor - Rough target Thanksgiving week. Request to go into BMC. Meeting needed to coordinate responsibility and timing, include BMC, IICC, Hyungmook & Jangpil - John Maclean to organize - planned for 11/8 Finishing layout on Anode, request to BMC to be sent 11/14. Cathode cutout layout tot follow line layout work.
| 4 | 2023-10-30 |  | LG | BMC |  |  |  |  | Corridor Sus-Plate installation, can Electrical Panels be placed on top of sus-plate? |  | 2023-11-03 | Hirano | Waiting on feedback from Hirano. Jinyoung contacting Hirano. Confirmed by LG, proceeding with plate throughout the corridor.
12 | 4 | 2023-10-31 |  | Conti | [5 empty] | Schneider Electric Install Manual Sub-Station Layout |  | 2023-11-07 | Ultium Jang Lee | Install manual same as U2?? LG to confirm U2 is correct for use at U3. 11/7 - on Copper Range now, and will use for U3
| 4 | 2023-10-31 |  | GM | [5 empty] | Platform Modification for Coaters (-200mm) - Who will perform the work? |  | 2023-11-07 | Norris | Norris to provide feedback. Norris ok to perform work on T&M.
13 | 2 |  |  | LG | [5 empty] | Duct work plan needed - integrate plan into Coater plan. |  | 2023-11-14 | IICC | Need to understand timing for drops and interconnects within Coater, how to execute (scaffolding?), and not slow the install of ovens, etc. 11/7 - getting Allied on-site and will put together a plan
14 | 2 | 2023-11-07 |  | Conti | Wooshin |  |  |  |  | Cable pull schedules Cable supply inventory |  | 2023-11-14 | Wooshin | LG to identify Wooshin team for support Wooshin team engaging, site visit 11/9. Info needed. Material is on-site - follow up with Jin Cable schedules requested 11/21 (TBC). 11/14 - provided tomorrow by Wooshin
15 | 2 | 2023-11-07 |  | Conti | Hirano |  |  |  |  | Installation books |  | 2023-11-14 | Hirano | LG to identify Hirano team for support 11/14 - Wooshin to provide Installation books provided by Hirano on 11/17.
16 | 4 | 2023-11-09 |  | Conti | [5 empty] | UPS System - What is deivery timing for Lines 2, 3, 4? Can they be accelerated to pull ahead RTSO? |  | 2023-11-14 | Ultium | Line 2 - 3 months (Feb) Line 3 - 6 months (May) Line 4 - no PO yet (Aug)
17 | 2 | 2023-11-09 |  | BMC | BMC |  |  |  |  | Area 200 Anode & Cathode Corridor #1 tank layouts needed |  | 2023-11-21 | TSI | Input for Sus Plate planning
18 | 1 | 2023-11-09 |  | Conti elec. | [5 empty] | J/R stk. #1 is fed from Coater 2 bus line. Cathode. System is needed for sample build |  | 2023-11-27 | Dunham/Ghafari | Move required…? DCR in preparation for 11/15 review
19 | 1 | 2023-11-09 |  | Conti elec. | [5 empty] | J/R conveyor #1 is fed from coater 4 bus line Cathode side System is needed for sample build |  | 2023-11-21 | Dunham/Ghafari | Move required…? DCR in preparation for 11/15 review
20 | 1 | 2023-11-09 |  | Conti elec. | [5 empty] | J/R RGV #1 is fed from coater bus line 4 Cathode side System is needed for sample build |  | 2023-11-21 | Dunham/Ghafari | Move required…? DCR in preparation for 11/15 review
21 | 2 | 2023-11-09 |  | Conti elec. | [5 empty] | CAD drawing for all FA for Panel layouts |  | 2023-11-21 | Avaco | Malyk to follow up with Avaco.
22 | 2 | 2023-11-09 |  | Conti elec. | [5 empty] | Install manuals for All FA equipment |  | 2023-11-21 | Avaco | Malyk to follow up with Avaco.
23 | 2 | 2023-11-09 |  | Conti elec. | [5 empty] | Which AGV's are required for sample build Anode and Cathode |  | 2023-11-21 | Avaco | Malyk to follow up with Avaco.
24 | 2 | 2023-11-09 |  | Conti elec. | [5 empty] | Layout of AGV'S Anode and cathode |  | 2023-11-21 | Cowintech | Malyk to follow up with Cowin Tech
25 | 2 | 2023-11-10 |  | Conti elec. | [5 empty] | Delivery dates for cables & tray - Anode & Cathode Line 1 |  | 2023-11-21 | Wooshin | 2 containers arrived. Content TBD. Request to move into building.
26 | 2 | 2023-11-10 |  | Conti elec. | [5 empty] | Cooridor Panel Layout Needed |  | 2023-11-21 | Conti | Rough space claim needed, Wooshin input to Panel layout needed.
27 | 2 | 2023-11-10 |  | Conti elec. | [5 empty] | Cable Tray Layout Drawings Needed |  | 2023-11-21 | Wooshin | Drawings to be released Wed 11/15 (Ovens) Top / Back - Released by 11/22 Incl Anode and Cathode
28 | 2 | 2023-11-10 |  | Norris | [5 empty] | DCR #002 - Can Daejin provide a modification drawing showing the cuts and steel additions that would be needed to complete this work. Also, who is providing the excess material Norris Brothers or Daejin. |  | Ongoing | Daejin | Draft 1 drawing submitted. Review closer to install date level of adjustment & field fit needed.
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45

## SRP
PRIORITY |  |  |  | UItium #3 Lansing Battery Plant Process Equipment Installation Project OPEN ISSUE TRACKING MATRIX - AREA 300
HIGH |  |  | 1
MED |  |  | 2
LOW |  |  | 3
CLOSED |  |  | 4 | [9 empty] | AS OF DATE: | 2023-11-14 17:21
NO. | PRIORITY | DATE ADDED | DATE CLOSED | ADDED BY | Company | OEM | Process Equipment | Process Equipment # | Process Equipment Location | OPEN ISSUE | RESOLUTION | DUE DATE | RESPONSIBILITY | COMMENTS
1 | 4 |  |  | VEC | VEC | MEC |  |  |  | Cooler Equipment Drawings/Foundation Design, need a structural steel support structure fabricated to set the cooler on |  | 2023-10-24 | VEC | VEC is definining scope to execute. Discuss steps next week. Need vendor drawings for Cooling Towers. Close issue for UC, MEC addressing.
2 | 3 |  |  | SAIL | VEC | MEC |  |  |  | Latest FOB dates to be communicated, track weekly for updates / changes. |  | 2023-11-14 | MEC | FOB dates received: Mid October (Absorber, Distallation, Reboiler, Module Skid) Tower Internal: Arrived in Lansing 10/23 Control Panel – ASK: early November requested - expedited, early Jan delivery ROS MEC: Middle December FOB - Early Feb ROS - VEC ok with delivery date. (ROS "Plan" per schedule is 1/1/24) Tank – Mid Dec or Jan - ROS Plan...?. MEC procures locally, Jon to clarify ROS dates with MEC. Absorber 11/1 Baltimore USA - ROS Plan: 11/30 Pumps/Distributor/Vacuum - ship date…? Plan ROS: 12/10/23 Tower Update: 11/25 to hit Baltimore. Further upate 11/13 once crossed Panama Canal. 3 day set up on crane, once towers are in port will trigger Crane mobilization. 2nd set of towers - update on timing weekly - critical input to Crane plan. Skid Module Timing - Week of 12/4 arrival. Departing Korea today, arrival LAX 11/14 (POR). Modules to arrive 11/14. 11/7 - no changes at this point per VEC VEC schedule updated to reflect latest ROS...? At Panama Canal - 7 days to Baltimore. Waiting on "green light" to pass. Matias discussing plan with SEVA. More next week. Update also on BOSS site visit to review delivery.
3 | 4 |  |  | VEC | VEC | MEC |  |  |  | Concrete foundations shown on the MEC model that need to be added to the pad for the cooling towers |  | 2023-10-24 | MEC | Close issue for UC, MEC addressing w/ 1)
| 3 |  |  | VEC | VEC | MEC |  |  |  | Final drawings needed for VEC to evaluate and kick off pre-fabrication work. |  | 2023-11-14 | MEC | Pipe Rack received Tank Yard and Recovery Pipiing next focus 10/17/23 - requesting drawings by 10/20 Vendor drawings received, 10/20, VEC reviewing content. Still needed: Tank yard ISO packages, Pipe support drawings Follow up needed Cooling Tower critical - need to add support drawaings. CT drawings uploaded to CR. Tank Yard Iso's next priority....Submission date to be confirmed by MEC. 11/7 - should have an answer this week 11/10 Tank yard received. 11/13 - Status? Electrical drawings needed. VEC need date first week of December. MEC on track to deliver by 12/1. Currently being worked on. | x
5 | 3 |  |  | VEC | VEC | MEC |  |  |  | Documentation requirements, reporting, QC (redlines, leak testing, continuity, etc) |  | 2023-11-06 | IICC | TBC | x
6 | 4 |  |  | VEC | VEC | MEC |  |  |  | Define trucking vendors for SRP equipment delivery. |  | 2023-10-20 | GM - Mathias | John to confirm with Mathias on vendor and delivery plan and loading needs for shipment and delivery. Boss identified as vendor. Requirements for transportation communicated.
7 | 3 |  |  | LGES | VEC | MEC |  |  |  | Design comparison for MI2 & UC3 designs for NMP circulation system, include level of insulation and gasket specifications. Ultium to evaluate design change request and specify details of change. |  | 2023-11-14 | MEC | Comparison data sent by 10/20. Need to know the full range of change Eric to organize an off-line meeting to level set and define next steps. Status / Next Steps…? Follow MI2 piping, insulate all electronic components. Heat Trace (?) NMP & Cooling Water Lines, All the tanks. LG asking for same as MI2. Scope to upgrade UC3 is clear. Quotation needed MEC + Install Team. ~ 2 weeks to quote. Follow up mtg MEC & VEC to clarify. 11/7 - VEC providing pricing next Tuesday for all three options 11/13 - ROM estimates received. Next steps?
8 | 3 |  |  | LGES | VEC | MEC |  |  |  | Provide definition around the gasket specification change teflon to metal for NMP circulation system (marked up drawing, change request, info from Poland gasket change, etc). Specification modfied by LG? Scope Definition needed - pre-assembled machines, site install only, etc... |  | 2023-11-14 | LG Minkoo | Team to evaluate and quote based on full scope of change request. Target would be spec and procure these locally to avoid any timing issues. Status / Next Steps…? VEC to quote based off Minkoo email. PID to be udpated after quotation. 11/13 - ROM estimates received. Next steps?
9 | 4 |  |  | LGES | VEC | MEC |  |  |  | Parts list for "Made in the USA" parts requested from LG |  | 2023-10-20 | MEC | Turb fun : Dec 2023. DI unit : Dec 2023. Corn roof tank : Jan 2024 Cooling tower : Feb 2024
10 | 1 |  |  | VEC | Ultium | MEC |  |  |  | Isolation Valves recommended for a "phased start up". Addition of four valves required. Approval of change and costs needed. |  | 2023-11-14 | LG Minkoo | IICC to send request to Minkoo to evaluate - complete DCR 002 sent to GM/LG/UC Add to drawings & prepare a cost estimate for material & install. Quote to be prepared. 11/13 - ROM estimates received. Next steps?
11 | 4 |  |  | VEC | Ultium | Ultium |  |  |  | Shower locations needed for SRP area. |  | 2023-11-06 | GM / Ultium | VEC - DCR #001 submitted including a proposed drawing based on UC2. Status? Final locations identified. Approved to proceed. Note: Water to be added once heat trace and insulation are installed.
12 | 1 |  |  | VEC | Ultium | Ultium |  |  |  | Laydown area, additional preparation including gravel install needed. |  | 2023-11-06 | GM / Ultium | 10/31 walk planned. Laydown space south of ring road needs to be prepared. BMC communicating "not in scope". Grade it flat, and that is all at this moment. Coordinate through Alan Plan to complete? 11/7 - Don following up with Alan
13 | 4 |  |  | VEC | GM |  |  |  |  | Meeting with Airgas needed - identify timing for work sequence |  | ongoing | GM: J. MacLean | John to organize - complete 1 week needed for setup / commissioning. Provide target date closer to NMP need date for system (1 mos prior). Install drawings received.
14 | 2 |  |  | VEC | BMC |  |  |  |  | Room Ready Dates for SRP building - RO Water Room and Control Panel Room |  | 2023-11-14 | BMC - Lonergan | BMC Plan? Required Dates from VEC? 11/7 - John setting up another meeting to review. VEC will give a need by date 11/13- Mid December rough need by date. John checking with BMC. Panels FOB 12/15 - potential to arrive at UC3 by 1/15 if trucked in early January from west coast. DI Water system available, supplied locally. Can be delivered once the RR date is established. DI Unit and Control panels need to be stored inside. 11/14 - dates Friday 11/17
15 | 2 |  |  | VEC | GM |  |  |  |  | Verify Key Dates ("by others"): Power on to SRP bus Nitrogen System Complete Boiler System Complete Plant NMP Feed Line Water supply to SRP area |  | 2023-11-14 | GM: J. MacLean | Clarification needed.
16 | 3 |  |  | VEC | Ultium |  |  |  |  | Confirm NMP need date for system commissioning based on RTSO progress Mixing/Coating |  | 2023-12-15 | GM: J. MacLean | Clarification needed.
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45

## Area 300
PRIORITY |  |  |  | UItium #3 Lansing Battery Plant Process Equipment Installation Project OPEN ISSUE TRACKING MATRIX - AREA 300
HIGH |  |  | 1
MED |  |  | 2
LOW |  |  | 3
CLOSED |  |  | 4 | [9 empty] | AS OF DATE: | 2023-11-14 17:21
NO. | PRIORITY | DATE ADDED | DATE CLOSED | ADDED BY | Company | OEM | Process Equipment | Process Equipment # | Process Equipment Location | OPEN ISSUE | RESOLUTION | DUE DATE | RESPONSIBILITY | COMMENTS
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45

## Area 400
PRIORITY |  |  |  | UItium #3 Lansing Battery Plant Process Equipment Installation Project OPEN ISSUE TRACKING MATRIX - AREA 400
HIGH |  |  | 1
MED |  |  | 2
LOW |  |  | 3
CLOSED |  |  | 4 | [9 empty] | AS OF DATE: | 2023-11-14 17:21
NO. | PRIORITY | DATE ADDED | DATE CLOSED | ADDED BY | Company | OEM | Process Equipment | Process Equipment # | Process Equipment Location | OPEN ISSUE | RESOLUTION | DUE DATE | RESPONSIBILITY | COMMENTS
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45

## Area 500
PRIORITY |  |  |  | UItium #3 Lansing Battery Plant Process Equipment Installation Project OPEN ISSUE TRACKING MATRIX - AREA 500
HIGH |  |  | 1
MED |  |  | 2
LOW |  |  | 3
CLOSED |  |  | 4 | [9 empty] | AS OF DATE: | 2023-11-14 17:21
NO. | PRIORITY | DATE ADDED | DATE CLOSED | ADDED BY | Company | OEM | Process Equipment | Process Equipment # | Process Equipment Location | OPEN ISSUE | RESOLUTION | DUE DATE | RESPONSIBILITY | COMMENTS
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45

## Miscellaneous
PRIORITY |  |  |  | UItium #3 Lansing Battery Plant Process Equipment Installation Project OPEN ISSUE TRACKING MATRIX - Miscellaneous
HIGH |  |  | 1
MED |  |  | 2
LOW |  |  | 3
CLOSED |  |  | 4 | [9 empty] | AS OF DATE: | 2023-11-14 17:21
NO. | PRIORITY | DATE ADDED | DATE CLOSED | ADDED BY | OEM | Contractor | Process Equipment | Process Equipment # | Process Equipment Location | OPEN ISSUE | RESOLUTION | DUE DATE | RESPONSIBILITY | COMMENTS
1
2
3
4
5
6
7
8
9
10
11
12
13
14
15
16
17
18
19
20
21
22
23
24
25
26
27
28
29
30
31
32
33
34
35
36
37
38
39
40
41
42
43
44
45