## Area 100
UItium #3 Lansing Battery Plant Process Equipment Installation Project OPEN ISSUE TRACKING MATRIX - AREA 100
1
2
3
|  | 4 |  |  |  |  | AS OF DATE: | 2024-03-01 08:01
PRIORITY | DATE ADDED | DATE CLOSED | ADDED BY | OPEN ISSUE | RESOLUTION | DUE DATE | RESPONSIBILITY | COMMENTS
1 | 2023-09-19 |  | PCE | Need BOM of ALL cable tray, strut, rod, etc ordered and timing of when balance of material will arrive onsite |  | 12/26/2023 now 1/12/2024 | CES/TSI | Delay anticipated for MCC rooms. Delay in mixing still being quantified. Order deadlines for Line 2 will be determined by SAIL/IICC/PCE to avoid ordering delays in future. 12/12: All lines ordered TSI to provide dates for arrival BOM for LInes 1-4 to be uploaded to CR today.(12/12) 12/19 PCE submitted spreadsheet detailing quantites received of tray and hardware PCE is in dire need of 1/2" threaded rod & hold down clamps. Will arrive 12/21, 22 Additional "RED" items identified 12/21. TSI to provide order & delivery dates. 1/16 - PCE to review what cable tray has been received. 1/23 - PCE to send material summary. Priorities for next deliveries. 1/30 - TSI working with PCE, positive feedback 2/6 - not providing vendor ETA. 2-3 weeks 2/16 - received some fittings, now waiting for ETA. Moving forward in other areas but could get started on this 2/20 - still waiting on fittings, no ETA yet been 3 weeks to date. Strut rod put in order today. Have to come back for the 9" fittings 2/27 - received 9" fittings, waiting on 9" tray. Big delivery last week - ok for a bit
4 | 2023-09-19 | 2024-01-09 | PCE | Need delivery date for Line 1 MCC Panels |  | 2023-12-26 | TSI | 09/19/23 - TSI has stated that LGENS has requested to modify MCC Panels. MCC Panels will be delayed per TSI to mid-November to ship from Korea. 9/26: Mid December arrival. Need to review schedule impact. 10/3/23: PCE / IICC to review impact on schedule. 10/10 - Continue to monitor schedule, depends on meeting other committments. 11/6: TSI to re-confirm. 11/14: Status? Shipped 11/1, roughly 45 days (11/16) * LGES requests the logistics team to transport the equipment by 12/1 (11/14) * GM SAIL (Don Jana) confirmed that transportation is necessary by 12/15 All panels arrived 11/27, except console panel. To be confirmed. PCE Install Date? 12/19 - PCE still needs confirmation of EMF panels - PCE & TSI searching. Location sent 12/26.
2 | 2023-09-19 |  | PCE | Need Limit switches and dustbin high level switches for DC Towers |  | 2023-01-02 | Ghafari | 09/19/23 - Capture accordingly to submit a DCR to Ghafari for review. 9/26: GF aware, meeting on 9/29. Update? 10/10: Roll into Ghafari weekly meeting 10/24 - Meeting, 10/27 will be able to give information to PCE Status:? 11/7 - review Friday 11/10 11/15 DCR review Part of DC Tower RFI package...? Package 30% reviewed today. To be posted by 12/1. Don to post to CR for PCE review. End of December supplier to be nominated. Check CR. Layouts needed, Quincy to follow up. 1/16 - End of Jan. TBD based on Environmental Equipment schedule.
4 | 2023-09-19 | 2024-01-16 | PCE | PCE needs terminals labeled in the touch panels & all RIO panels to be installed on the 2nd floor on Anode & Cathode (this came up at U2 and just trying to get ahead of it if it becomes and issue on U3) |  | 2023-12-26 | TSI | 09/19/23 - Need panel drawings labled completely from TSI. TSI to review their team members internally and report back to the team. 9/26/23 - Continue to monitor to avoid in future. 11/.29: All RIO panels still need to be labeled. PCE reviewed panels this week - not labeled. Support from TSI Needed to label. 12/1 TSI engineer coming to support labels for RIO panels. Target completion by 12/7. (12/01) Name tag : TSI member is putting tags on it.(12/1~). Labeling on-going. Continue to monitor. 1/9/24 - monitor going forward
4 | 2023-10-02 |  | PCE | List of Field Devices identifying which panels they connect to. |  | 2023-12-26 | TSI | 10/3 - PID uploaded, PCE to review. 10/10: Need a list of field devices by skid to be installed by 10/31 Instrument list uploaded on CR. Updated list for Anode uploaded, PCE to review and provide feedback. TSI to provide file path. PCE looking for device numbers to plan term and pull packages. PCE to check ISO's. 10/31 - device list in 3 weeks - 11/21 list 11/7 - TSI had a discussion with PCE regarding to clarify request. 11/21 - draft version sent today, P&ID sent, adding what is in/out TSI is adding more to the list. What has/hasnt been installed. TSI to provide information within a week 11/29: Need to filter list by ship lose, P&ID shows dividing line for what is on/off skid. PCE to review if designation is enough. (12/01) Instrument List : Uploaded on Copper Range(11/28). 12/12: PCE feedback: Incomplete. Yubin to follow up on completing this per PCE. 12/19 - Yubeen from TSI is working on marking up P&IDs to complete the list of field devices. Continue to complete list. 1/9/24 - anode cathode complete by 1/12/24 1/16 - Yubeen sent first draft, and PCE to review. Leave open 1 more week
1 | 2023-10-03 |  | Conti | Schedule for Drawing Releases? |  | 2023-11-28 | TSI | Piping Drawing Release Plan: Support Iso Anode 2F 9/27 9/27 Cathode 2F 10/15 - 10/30 10/15 - 10/30 Anode 1F 10/30 10/20 10/30 - 10/20 Cathode 1F 10/30 - 10/30 10/30 - 10/30 Coater 11/5 11/15 → CAD 2D Layout (~11/28), 3D/ISO(~12/19), Support 2D drawing(~12/22) Pipe Matrix to be reposted today 11/29 (incomplete) Lines 1 & 2 need to be 100% Design Freeze. IICC requesting LG support to enforce this with TSI. Revisions + On Holds + Missing will result in a Line 1 Installation Delay. 22 new drawings uploaded to CR 12/11. Changes after freeze date will be rejected and added to Continuous Improvement work/budget. 12/26: Anode ISO's - released however some still on-hold Cathode ISO's - 12/27 release - still with some on-hold Piping Support - 12/28 release Corridor Layout still open - TSI to provide date. 1/9/24 - on hold pipe will be removed. 1/16 - releases the 1/19 & 1/26 1/23 - TSI needs to supply drawings keep ahead of Conti. 1/30 - detail drawing released 2/16 for Anode (All three areas), 4,000 tube by tmrw 1/31 2/6 - anode second floor uploaded, anode 2/16. 2/13 - anode first floor uploaded. detailed support drawings. Coater corridor anode 2/16 2/20 - waiting on 60 more cathode 1st floor. 3D model 2/27 anode, 3/12 cathode 3/19 - final date for pipe supports 2/27 - TSI has the 3D drawing for coater corridor rework - Anode first. 3/12 still date for cathode. Line 2 - May 5th and final release 5/25
2 | 2023-10-10 |  | PCE | Need schematics for AC / DC towers |  | 2023-01-09 | Ghafari | Last week of December for supplier decision and schematic availability. Interface meeting btw TSI & Ghafari will be needed. Assumes all AC/DC towers. 1/16 - Quincy to follow up with Don
4 | 2023-10-13 | 2024-02-20 | BMC | Core Holes |  | 2023-12-26 | TSI | 11/21: Three interferences found. DCR submitted. TSI to provide alternative locations. 4th interference found, revised drawing to be released tomorrow. 11/29: Clarifcation of additional 15 inch core holes location in question. --> New DCR to be defined. DCR for 11/21 interferences approved. by TSI. (12/01) TSI will reply about DCR(#15) (~12/4) 15" floor core holes - BMC to approve location and buy off. Timing TBD 12/19: Line 2 Anode/Cathode core hole locations needed. I Line 2 layout - TSI to dimension based on Brass Datum's installed, request and provide date. 12/26 Plan: 1/3 - Receive drawings 1/9 - FMG to drill. 1/23: On track for 1/23 for anode and 1/30 for cathode core holes - Line 2 only 1/30 - layout for cathode tomorrow, 2 interferences on the Anode side 2/6 - TSI and BMC walked and agreed on interferences, waiting on cathode drip pan drawings release date 2/7 2/16 - two holes interference on cathode. BMC to mark up drawing, showing what the move needs to be. FMG to do 15 holes on cathode line 1. 2/20 - BMC and PCE walking this afternoon to establish core holes needed to drill. Line 2 ongoing
4 | 2023-11-20 |  | PCE | SRP Fiber Material: Has the fiber, converters, fan out kits etc been ordered? Need delivery / timing and cut sheets on all parts ordered |  | 12/26/2023 now 1/20/2024 | TSI | To be clarified PCE & IICC Cathode PLC panel out to SRP PLC panels Will go through profinet - send term locations next week Has a material for this SOW been ordered? Answer next week MEC/TSI review next week on hand-off (12/01) A meeting about communicating between Mixer and SRP will be held on 6th of December.(LG, TSI, MEC) Cable/Tray to be purchased and shppped from Korea. TSI providing material, drawings on Copper Range...Install TBD? Shipping dates to be provided next week (TSI). 12/26: To be checked with HQ. Yubeen to provide dates. 1/9/24 - air freight and here by 1/20 1/16 - fiber was received, not correct. Yubeen checking on converters and fan out kits
2 | 2023-11-20 |  | PCE | SRP Fiber Run - Are there drawings / schematics / cable schedules available? 2nd floor MCC room out to SRP bldg. Material? TSI to provide data sheet |  | 2023-12-26 | TSI | To be clarified PCE & IICC Confirm exact SOW - SRP end TBD John MacLean to follow up with UC2 Execution team. MEC/TSI review next week on hand-off. TSI providing material --> Drawing status? 12/26: To be checked with HQ. Yubeen to provide dates. 1/9/24 - PCE and TSI speaking after whiteboard meeting Wednesday 1/16 - Yubeen to check on timing 1/23 - Yubeen checking on drawings + converters and fan out kits. 1/30 - names of the panels and where to land once at the panel. Materials as well, converters and fan out kits no information on SRP cable schedule released 2/2 2/6 - PCE has a prelim drawing. Jang checking on this. Has to align with RTSO for cathode 2/13 - PCE has not received, Quincy following up with Jang 2/20 - Jang having meeting today at 7pm with MCE, PCE just needs name of panel. TSI to provide data sheet this week
4 | 2023-12-01 | 2024-02-20 | IICC | Monorail layout for Lines 2, 3, 4 needed, When is material going to be here? |  | 2023-01-09 | TSI / Mazella | Layout requested to continue to progress the abatement process and install monorails earlier on lines 2-4. Line 1 2nd floor released Anode/Cathode. Working on Lines 2-4. Date needed from TSI:? Mazzella to prepare layout for lines 2-4 by 1/9. Anode and Cathode. 1/9/24 - TSI to give us an answer later today 1/16 - hoist early march for Line 1. Power rail coming as well? Kevin Moon is checking 1/30 - TSI to get drawings 2/13 - replacement beams will arrive this friday , and all beam connections
4 | 2023-12-05 | 2024-01-30 | PCE | Need installation date for panel designated for IQC Room - Panel PLF6-1-2 |  | 2023-12-26 | Superior | Location changed. Removed, not reinstalled. Superior waiting on change order. Review with Alan Thompson --> Quincy tracking, provide status.
4 | 2023-12-05 | 2024-01-30 | PCE | What is the red tag date for the IQC Room? |  | TBD | SAIL/GM | Align with Mixing TBD
4 | 2023-12-05 | 2024-01-09 | PCE | In Utility Matrix, the MCCB for each PD Mixer panel is sized for 500A, but at UC2, it was increased to 600A due to breaker sizing required by code. By the FLA shown in the Utility Matrix, it should be increased to 600A. Need a confirmed Ultility Matrix for Coater Corridor as well. |  | 2023-12-22 | TSI | TSI to double check PCE planning for 600a 500a confirmed as correct, motor spec is lower than received. Reflects UC2 Line 3. Utility matrix going to be re-issued - TSI to re-issue. Due by 12/22. PCE to issue material order by 12/29. 12/26: TSI released and confirmed from LG/ENS to send to LG construction team.
4 | 2023-12-12 | 2024-01-09 | PCE | There are discrepancies between the bus schedules and what is needed for install for the High Pressure Cleaners and the Water Heaters - on the bus schedules there are only (4) High Pressure cleaners shown with (6) to install and there are only (8) Water Heaters shown with (12) to install |  | 2023-12-26 | Superior | Superior to update bus schedules.
4 | 2023-12-12 | 2024-01-16 | PCE | The CAD file showing the IQC room does not match the actual IQC Room dimensions / layout. We need the CAD file adjusted to reflect the true layout of the IQC Room |  | 2023-12-12 | IPD | Follow up with Quincy on finding support at IPD.
4 |  | 2024-01-16 | PCE | Fire Sprinkler Interference - Cathode Cable Tray |  | 2023-12-26 |  | PCE proposal from UC2 to be reviewed after the meeting. TSI to review proposal from PCE 12/13. 1/9/24 - shambaugh to relocate, and PCE to install a cover
4 |  | 2024-01-09 | TSI | Cathode Pre-Mixer 1-3 damaged, to be replaced. FOB end of January out of Korea (TBC by TSI). |  | 2023-12-26 | SAIL | Targeted install date was 1/8-1/12 When will 2-3 be installed? Isolation valves? 1) Need build/ship date from TSI. Mixer and Tank module to ship in April - onsite in June (?) 2) Team to evaluate impact on Line 1 Cathode install (BMC/PCE/Conti M) Line 3 PO done, on-order. TSI to provide more detail on expediting replacment and scope. Ship date for 3-3. Can the replacement be shipped piece meal? Use existing skid as a potential? TSI to provide drawing of 3-3 for comparison.
4 | 2023-12-15 | 2024-01-16 | BMC | Missing Gantry Hoist for 1-2, 1-3, 1-4. When will these ship and be on site? Only 1-1 on-site – |  | 2023-12-26 | TSI | Delivery date needed ASAP. Material on-site. Need drawings, install direction and anchors. Is the Mazella beam on-site?
4 | 2023-12-15 | 2024-02-13 | BMC | Motor Cover Plate (black & yellow striped floor plate) is slightly too small. The lip of the covers sit on the concrete floor about ½” around the edges. There is enough play in the steel beam supports under the plate that this could potentially fall into the hole if bumped. (permanent floor covering provided by TSI – timing – TBD). Plan needed to address. |  | 2023-01-09 | TSI | TSI to review and provide plan to address. (Note: Issue was noticed on Anode 1-2: we have barricades around this area to keep people off the plate due to this issue.) TSI - Propose to add shims. Looking for more long term solution. 12/26: TSI to provide short term / long term plan of action to address. Field Fix? Re-order in larger size? 1/9/24 - TSI having one last discussion tomorrow and will proceed 1/16 - Yubeen to meet with Minboo tomorrow 130 pm 1/23 - Still negotiating with LG. BMC offering to weld in new material as a possible resolution. BMC to submit for TSI to review and approve. 1/30 - Yubeen to respond in DCR format
4 | 2023-12-15 | 2024-01-09 | BMC | Need updated Platform drawings / install manual. The drawings we have on hand do not match the material on site. |  | 2023-12-26 | TSI | Need updated drawings to match material on-site + installation manuals, torque specifications, etc.
4 | 2023-12-19 | 2024-01-09 | PCE | Cathode sprinkler head moves (2x @ E9.5 column 1F) |  | 2023-12-26 | Shambaugh | Awaiting confirmation
4 | 2023-12-19 | 2024-01-09 | PCE | RO skid disconnect / piping install clash. |  | 2023-01-09 | TSI | TSI to propose solution. TSI to mark proposed disconnect location on floor for rewview with PCE.
3 | 2023-12-19 |  | GM | Confirm PCE to use cable schedule over schematic when there is a discrepancy. When will schematics be updated? |  | 2024-02-19 | TSI | DCR to be issued, TSI to clarify direction to install team GM/Ultium issue 1/30 - only the pumps will be changed. Updated after cathode cable schedule 2/6 - focusing on line 2 cable schedule. 2/19 release date 2/16 - schematics updated 2/23 to match cable schedule 2/27 - still updating schematics for the panels
4 | 2023-12-19 | 2024-02-13 | PCE | Use of Junction boxes for all PD & BTN mixers. |  | 2023-12-26 | TSI | Direction, layout (SOW) plan requested from TSI. PCE to issue DCR. 1/9/24 - need the full scope of work. Walk down tomorrow morning after whiteboard 1/16 - waiting for material to arrive 1/20, then walk again to spot 1/23: Arrived by air 1/18. TSI to check and inventory. 1/30 - received 17 for anode and cathode. Friday 2/2/24 2/6 - received today, next week install 2/16 - received today
4 | 2023-12-19 |  | Conti Elec | Coater AC5 panel drives (6) missing - track for future delivery |  | 2024-04-01 | TSI | Continue to track.
4 | 2023-12-26 | 2024-02-27 | IICC | Pipe Labeling for mechanical install. Who is providing labels? |  | 2023-01-09 | TSI | TSI making the labels. Will provide lead time 1/16 - 2 weeks from now. 2/9 arrival 1/23: 2/9 or 2/16 delivery date…20k labels for Line 1 to be shipped. 1/30 - TSI to check fabrication time, and air shipment time 2/6 - still on track for 2/16 2/13 - TSI to contact Korea this evening. Quincy has a meeting regarding the Ultium standard 2/20 - IICC to look into label maker
2 | 2024-01-09 |  | BMC | GAD for Line 2, 3, 4 - Release Dates |  |  | TSI | 1/16 - released after core hole drawings, 1/31 1/23: Yubeen dates: Anode 1F/2F - 1/29 Anode Corr - 2/1 Cathode 1F/2F - 2/7 Cathode Corr - 2/15 1/30 - Anode first and second floor received. Cathode still on track 2/13 - TSI to call tonight and check on the GAD drawings 2/20 - line 3 GAD end of March, line 2 complete plus 45 days 2/27 -
4 | 2024-01-12 | 2024-01-30 | BMC | Anode #1-1 between duct and wall - Gap of 5mm, finish with chemical resistant silicone |  |  | TSI | Looking for second option. Quincy talking with Ultium. TSI speaking with team 1/23: Team met, fill small gaps with Silicone. Specs to be prvoided by GM Quincy.
2 | 2024-01-16 |  | BMC | Mazella Rail - all layouts and all materials on site for Lines 2-4 Anode and Cathode. This work could be going on now |  |  | TSI | Need confirmed delivery dates & up to date drawings. 1/26 - in person meeting. With Mazella visiting. 1/30 - Anode 1-2, 1-3 beams to short. Cathode - all beams 2ft to long. Touch up paint - get with skyline 2/6 TSI headquarters reviewing and will report out 2/20 - BMC pushing to get schedule on arrival dates 2/27 - 5 weeks from 2/26 - ETA 3/18 for Lines 2 & 3 monorail
4 | 2024-01-16 | 2024-02-20 | BMC | SUS plate fill in - requested to fill in behind AHUs and door openings between rooms. 1) 6mm vs 4mm between corridor and mixing room 2) where is fill in required between control room, component cleaning room, loading dock area, etc? |  |  | TSI | Being requested by LG Mr.Kung. Quincy to follow up 1/23: Plate to be left out. Alternative proposal? TSI/GM to define. 1/30 - proceed with the toe kick per GM Leadership 2/6 - Quincy and Kevin B going to walk this scope 2/13 - DCR to be made
4 | 2024-01-16 |  | BMC/PCE | Lines 2-4 Core Hole Drawings - Line 2 Anode - 1/23 Line 2 Cathode - 1/30? |  |  | TSI | Line 2 tracked. 3 & 4 TBD. Repeat item.
4 | 2024-01-16 | 2024-02-20 | BMC | Door Fill Ins. Between rooms - what is the detail |  |  | TSI | Define transitions for doors. 6mm plate as soltuion. 1/30 - walk thru with Quincy
4 | 2024-01-16 | 2024-02-13 | IICC | Installation sequence for the coater corridor |  |  | TSI
4 | 2024-01-22 | 2024-02-13 | BMC | Anode 2F - Gantry Hoist Structures. Had to pack multiple spare shims that now leave a gap between the base plate and floor. Is this acceptable? |  | 2024-02-13 | TSI | TSI to make recommendation based on U2. 2/6 - on site 2/13
2 | 2024-01-22 |  | BMC | Area 200 Equipment List / Information Requested: 1) GAD Drawings 2) SignOff Sheets for each piece of equipment 3) Drip Pans – Identification, layout, crate info 4) Equipment Elevations 5) Sequence of Insall – which units are required per line, which are needed for “Sample Build” 6) Assistance in Building Material Request Sheets, can build once GAD’s received and can get with K. Moon to help populate information (crate info) like we did for Area 100 Equipment. |  | 2024-02-09 | TSI | 50% information prepared. BMC & TSI discussing. Include delivery schedule for Lines 2-4. Line 1 here. TSI to review with UC2 and provide feedback. 1/30. 1/30 - elevations, sign off sheets, 2/6 - TSI answer by Friday 2/13 - TSI one more day 2/20 - TSI sending by now 2/27 - Juno to send to BMC
4
4 | 2024-01-23 | 2024-01-30 | PCE | Missing trough to RIO panel - |  |  | TSI
4 | 2024-01-23 | 2024-02-20 | Conti | Piping arrangement drawing for SRP trestle needed for cable tray and utilities. |  |  | TSI | 1/30 - pulling down drawings from BIM to CR - 2/13 - Conti moving forward
3 | 2024-01-30 |  | IICC | White Steel Support - Conti Mechanical/Paynecrest. What was done at UC2? |  |  |  | Line 1 complete, working on material for lines 2-4
2 | 2024-01-30 |  | PCE | Installation dates for panels powering the AC/DC Tower |  |  |  | Structure up
4 | 2024-01-30 | 2024-02-20 | PCE | Line 2 - cable schedule dates, one month need date |  | 2024-02-19 | TSI | Received
4 | 2024-01-30 | 2024-02-06 | Conti | Polishing Procedure on the DI Water - Any location there is a butt weld |  |  | TSI/Quincy | 1/30 - TSI to ask designer
4 | 2024-01-30 | 2024-02-13 | Allied | Single Unit Strut - Wednesday arrival |  |  | TSI | 2/6 - hardware is on site, sent to the anode second floor with Conti material. TSI to speak with Allied
1 | 2024-01-30 |  | Allied | Updated Drawings - Support hanger drawings |  |  |  | Anode complete, Cathode not complete yet
2 | 2024-02-05 |  | PCE | Damage Type VC3GUN Disconnect on AADR132 Skid - Need Replacement. Second floor anode |  |  | TSI | TSI to look at this item 2/13 - TSI to order new one 2/20 - PCE to speak with team 2/27 - Has not been replaced, TSI looking into it. TSI needs to tell us what needs to be done here. Conduit drops in a week and a half
4 | 2024-02-06 | 2024-02-27 | PCE | Concrete/Dirt finish work |  |  | GM | 2/20 - follow up with GM
1 | 2024-02-06 |  | BMC | Columns interferences with Drip Pans in Corridor - Line 1 |  | 2/7/2024 now 2/16/24 | TSI | 2/13 - layout different than the GAD. 2/20 - TSI doing a revision, will write an email to BMC 2/27 - TSI needs to revise the GAD for corridor
3 | 2024-02-06 |  | Conti Fire | Temp walls in the boiler rooms - Elevation of pipe and how high it needs to go. Cathode 4 lines |  |  |  | 2/20 - anode up and over, waiting on cathode for the tanks
1 | 2023-10-02 |  | Conti | Hanger layout Drawings for Cathode and Anode Coater Corridors requested. |  | 2023-12-26 | TSI | Support 11/5; Iso 11/15 Design Version #28 will be released in 2 weeks. Impact timing TBD! (11/22) Drawing release plan : Mixer room, Corridor, Coader Top/Back (Cathode/anode) → CAD 2D Layout (~11/28), 3D/ISO(~12/19), Support 2D drawing(~12/22) All Coater Corridor 100% on-hold. Delay TBD. Status: Conti to check 12/21 deliveries per TSI email on Copper Range. 2/13 - redesign Anode 2/15, cathode 2/22. Final submission - Anode 2/27, and cathode 3/7 2/27 - 3/5 anode and 3/19
3 | 2024-02-07 |  | PCE | Tracking update for Netzsch and EMF Cables |  | 2024-02-29 | TSI | 2/13 - Netzsch received, still waiting on the EMF cables 2/20 - PCE need EMF cables in a couple weeks
3 | 2024-01-23 |  | Conti E | Cable Pull Schedules needed for Coater Corridor equipment. |  | 2024-03-13 | TSI | 2/6 - TSI to field check. Conti checked and its not even close 2/13 - TSI to fix 2/27 - Conti electric to check CR
2 | 2024-02-13 |  | BMC | Anode second floor drip pan - wrong orientation |  |  | TSI | 2/13 - currently 3 week out, using same as UC2 2/20 - in the works 2/27 - order in and waiting on material - 10 day delivery expected 3/8
1 | 2024-02-13 |  | BMC | Back coater mezz - clashing with platform currently existing |  |  | TSI/GM | Tank location, equipment not same as design change 2/20 - location will be changed.
2 | 2024-02-13 |  | Conti | Isolation valves for Cathode |  |  | GM | Conti submitted a quote to IICC
4 | 2024-02-15 | 2024-02-20 | Allied Vent | Ship all remaining spiral and fittings |  |  | TSI
1 | 2024-02-16 |  | Conti E | IFC Drawings - don’t match, Equipment schedules |  |  | Dunham/Superior
2 | 2024-02-27 |  | BMC | OHT Rail Installation |  |  | Rotem | Bolts are the wrong size, using multiple washers to fill, double lock washers, double jam nuts Spacing between supports Main rail to sub beam connection missing load rating signage on rails 2/27 - Rotem looking into it and providing feedback by 3/5
2 | 2024-02-27 |  | PCE | Cathode 1-2 Slurry Buffer Tank - Disconnect Switch Damage

## Area 200
UItium #3 Lansing Battery Plant Process Equipment Installation Project OPEN ISSUE TRACKING MATRIX - AREA 200
1
2
3
|  | 4 |  |  |  |  | AS OF DATE: | 2024-03-01 08:01
PRIORITY | DATE ADDED | DATE CLOSED | ADDED BY | OPEN ISSUE | RESOLUTION | DUE DATE | RESPONSIBILITY | COMMENTS
3 | 2023-10-16 |  | Norris | Centerlines for Cathode Line 2 needed, confirm alignment and or additional measures to be taken. Solutions to Coater / Column clash - pit location |  | 2023-12-26 | Daejin / Norris | 11/14 - Jangpill, and construction team to review this further. GM, IPD, Sail team, and LG construction for this discussion Daejin to provide model overlaying coaters (Anode Lines 2 & 4) in building space accounting for all building columns. -> Cathode line 1 by 11/17, rest of the lines by end of next week --> Jangpill & Charlie evaluating column relocation Cathode Lines 2 & 4 (cost and timing). Due: 11/22 11/21 - Daejin to provide answer by Friday. Follow up meeting 11/29, 30 J. Maclean to schedule. (11/20.23) * Cathode line #1 center line 40mm shift layout drawing completed and copper range upload / Provided to Norris (11/16) (11/27.23) * Drawings applied with the line 2~4 avoidance plan To be uploaded copper range today (11/27) No building column move, Daejin updating drawings today for final locations. Follow up meeting to be scheduled - J. Maclean by 12/1. Meeting held. Team is aligned on shifts. Drawings to be updated with dimensions off building columns. (12/04.23) * Cathode #2 Top pit Stage revision drawing Copper range upload completed (12/04) * Cathode/Anode #2 line marking drawing in progress (~12/15) Follow up when drawings released on CR. Line 2 uploaded 12/15 - verify 1/16 - still need to verify centerlines. Check drawings 1/23 - Norris asking to put center lines in, discuss at White Board logistics to clear space and time. 1/30 - Daejin working on drawings still 2/6 - centerlines end of this week. Cathode received, unsure if its final line 2/13 - anode done, and verifying centerline on cathode 2/20 - getting shot today on cathode. anode - holes and elevation currently 2/27 - cathode - centerlines complete, columns are not. Not holding anything up currently
4 | 2023-11-07 | 2024-02-13 | Conti E | Cable pull schedules Cable supply inventory |  | 12/26/2023 now 1/12/23 | Wooshin | 12/5: LG requesting IICC to follow Wooshin direction. IICC requesting Hirano agreement in writing to deviate from Hirano drawings. Hirano drawings will not be updated to reflect Wooshin changes. 12/12: Multiple clarifications ongoing...when will cable pull schedule be frozen? (12/11.23) * Confirm that Hirano agrees to the Wooshin installation guide - If necessary, a mail with the content will be sent Clean Up Pass needed to incorporate all changes. Wooshin date: ? 12/15 Lastest update 12/15 uploaded to Copper Range. 12/19 committed to as Final Date for changes. Need Wooshin feedback for final design freeze. Changes from Hirano submitted 12/19 Wooshin proposes 12/29 for final cable schedule To accelerate, Wooshin will release pull schedule by panel (17 panels AC1:? , AC2: ?...) Changes after freeze date will be rejected and added to Continuous Improvement work/budget. 179 corrections needed in 1 panel 1/16 - everything uploaded to CR 1/15 - Conti digging through this now Cable matrix will be requested next 1/23: Winder/Un-winder information needed. Conti working through info with Wooshin. C1/C2 need to be addressed. Cathode submission needed. Wooshin to start. 1/30 - Wooshin to submit by Friday 2/6 - Conti still working through it
4 | 2023-11-07 | 2024-02-13 | Conti E | Termination Books - all fall under line item 10 |  | 1/9/2023 now 1/12/23 | Hirano | LG to identify Hirano team for support 11/14 - Wooshin to provide Installation books provided by Hirano on 11/17. Cover in 11/21 meeting with Wooshin. Hirano claims all info with Wooshin. (11/27.23) * Documents sharing completed (11/24) Anode / Cathode sumbitted. Conti Feedback? Escalation meeting needed. Revisit after cable schedule update
4 | 2023-11-09 | 2024-01-30 | BMC | Area 200 Anode & Cathode Corridor #1 tank layouts needed |  | 2023-12-26 | TSI | Input for Sus Plate planning TSI reworkng tank and water heater layouts. Two weeks to complete. 12/22 completion target. GAD drawings to be submitted 1/24
4 | 2023-11-10 | 2024-01-11 | Conti elec. | Delivery dates for cables & tray - Anode & Cathode Line 1 |  | 12/26/2023 now 1/29/2023 | Wooshin | 2 containers arrived. Content TBD. Request to move into building. In building, need to inventory. (11/20.23) * Completed move into the factory (located in Cathode No. 2) * Wooshin to check parts (11/27) Packing list provided by Wooshin Status:? Final check of fittings in the ovens. Conti providing feedback Confirm by 12/15 based on oven invetory. Conti checking Ovens this week. Potential High Risk if not part of Oven delivery. Ovens being unpacked, ladder tray, fittings, etc. still TBD. Conti & Wooshin reviewing delivery contents to determine missing parts. Conti only waiting on the ladder tray fittings - 3 or 4 week of Jan
4 | 2023-11-10 | 2024-01-09 | Conti elec. | Cable Tray Layout Drawings Needed |  | 2023-12-26 | Wooshin | Drawings to be released Wed 11/15 (Ovens) - submitted. Top / Back - Released by 11/22 Incl Anode and Cathode Update tomorrow with Wooshin (11/20.23) * Oven part completed data sharing (11/17) * Top/Back part is working on (11/27.23) * Drawing sharing completed Wooshin requesting two weeks to complete Top/Back designs. 12/5: Wooshin communicated "concept only" for tray layout...? Conti to dimension to proceed. Building to current drawing. 12/19: Top and Back cable tray drawings not available. Wooshin to provide ASAP. 12/26: Same status as 12/19. Design complete, checking with OEMs. Plan to finish reviews this week, Wooshin to submit to Copper Range by 1/3.
4 | 2023-11-21 | 2024-01-09 | JEG | JEG kick off, expedite pipe design / install download get JEG mobilized starting 12/4. |  | 2023-12-26 | Joong Wong | Layout/Drawings, BOM, Installation Manuals, Welding Specficiations, Fabrication Sheets. Welding spec to be submitted for approval. IICC to ask JW for approval. JW to approve welding spec. JEG following IPD welding spec
4 | 2023-11-21 |  | IICC | Fire suppression system definition needed. Areas 100-500 requeted from Conti Fire. |  | 2023-12-26 | IICC / Conti | Kick Off 11/27 Conti requesting CAD models and building tie in definition needed. 3 weeks for fabrication needed to start install Conti FP to start with UC2 design. Kick off held, site visit 11/30. Conti working with UC3 models Pre-fab ongoing, will mobilize week of 12/4 Contacts for "rest of plant" needed.
4 | 2023-12-12 |  | Conti elec. | Terminal Boxes needed to address cable layout revisions 1. We need updated drawings showing where these boxes are supposed to be installed. 2. We need the Cable Matrix updated to show cables going from the panels to Terminal boxes. 3. We will need to have the Added Cables from the new Terminal Boxes to the field devices added to the Cable Matrix. 4. Termination info needed. |  | 2023-01-03 | Wooshin | Wooshin to provide material. Quantity: 150+ Need by date:12/26 Status needed by 12/12 COB. 78 sent with Ovens. Wooshin to locate. Remaining terminal boxes to be ordered by Wooshin 12/19: 1-4 Due as part of the final 12/29 submission Wooshin requesting 12/29 + 2-3 days to finalize.
4 | 2023-12-04 | 2024-01-30 | Conti elec. | Coater Lights missing - |  | 2023-12-20 | Wooshin | To be delivered to Conti Warehouse by 12/20. Delivery date TBC. 1/9/24 - back order till end of Jan. 1/16 - received 119 of 140 1/23 - Conti to recheck inventory to close
1 | 2023-12-15 |  | JEG | Hot Oil Piping Support Design needed to cost and fabricate to address scope gap. Field Order needed |  | 2023-12-26 | Joong Wong / Ghafari / LG | Design needed from Joong Wong. 1/16 - Joongwon to provide 12" drawings today. Not the 14". Will look at the drawings once received JEG to do engineering work to support. FO approval needed including the material for water fall piping. 2/13 - back coater wall will block JEG, lead time concerns, 76 welds
4 | 2023-12-19 | 2024-01-16 | JEG | Identify 1F bridge work durations with and without ovens/blowers installed. Net savings? |  | 2023-01-09 | JEG / Conti E / Conti FP / Allied | To be discussed in Coater team meeting on 12/20. JEG reviewing 10" weld timing and branch piping. 1/9/24 - next Tuesday to provide follow up/answer
4 | 2023-12-19 |  | Conti elec. | e-Stops crate locations to be provided by Hirano |  | 2023-12-26 | Hirano | Hirano follow up requested. Wooshin to follow up with Hirano and provide feedback. Wooshin checking inventory, plan to turnover to Conti 1/5. 1/9/24 - Wooshin has not turned over anything, just has the stands 1/16 - Conti received the crate information and will go through tomorrow
4 | 2023-12-26 | 2024-01-16 | Conti elec. | Need confirmation on the Hirano drawings posted to Copper Range, Is this the final release? Is there another release planned? |  | 2023-12-26 | Hirano | Released for Construction.
4 | 2023-12-21 |  | Joong Wong | JW requesting support for discolored ductwork damaged in shipment. |  | 2023-12-26 | IICC | IICC / subs cannot support - not budgeted for time and/or funding. 1/9/24 - reevaluate this issue Cleaning process to address.
2 | 2023-12-21 |  | AMS | Duct work missing scope - need drawings / installation manuals to evaluate work and timing. Cathode Fix |  | 2023-12-26 | Hirano | Hirano to submit ASAP. Mfg drawings available, Hirano to describe install with separate document. Hirano to UC 12/27, UC to IICC 12/28. 1/24 - floor walk later today 2/13 - drawings received, evaluate work and timing 2/20 - anode approved design by Minkoo, cathode still being worked on
4 | 2023-12-21 | 2024-01-09 | GM | Roll Map define work scope, timing, plans to support. |  |  | LG / IICC
4 | 2023-12-21 | 2024-01-09 |  | Avaco Kick Off planned for 12/27 for FA
4 | 2023-12-21 |  | Conti Elec | Panel drawings needed Anode/Cathode |  | 2023-12-26 | Hirano | Part of 12/29 final submission. Follow up early January. Final drawings submitted, date stamped for December '23.
4 | 2023-12-26 | 2024-01-16 | IICC | Delivery / Install timing for dust collectors, FFU, EFU |  | 2023-01-09 | Daejin | Sitting inside the building currently.
3 | 2023-12-26 |  | IICC | Pipe Labeling for mechanical install. Who is providing labels? |  | 2023-01-09 | Joong Wong | IICC to follow up with JW. 1/9/24 - DCR sent out, and JW reviewing this currently 1/16 - Joongwon will sign off on the DCR 1/23: JW to supply labels, 2 mos for delivery to UC3. Need to review standard for consistency. Clarify nomenclature for printing. Investigate option to make locally- 1/30 - IICC label machine? 2/6 - marketing services inc (julie). Be here mid Feb just for duct. Delivery install plan for all duct work piping. Hot Oil piping 2/13 - arriving on-site 2/16 2/20 - duct labels received, pipe labeling none received yet
4 | 2023-12-26 | 2024-01-09 | Conti elec | Define Roll Press Schedule, List of Contractors, OEMs to start preparations. |  | 2023-01-09 | IICC
4 | 2024-01-09 | 2024-01-16 | AMS | IPD duct work interference. Chase with facility taking a look at it and will get it handled per Joe Arnold
4 | 2024-01-09 |  | Conti Elec | Wooshin wants conti to hold off on tray above ovens |  |  |  | 2nd floor approved to proceed
4 | 2024-01-16 | 2024-01-30 | AMS | IPD duct work to Joongwon duct work not the same size. |  |  | GM | AMS prepared to fabricate/install right away To be bundled with "duct gaps" FO and address accordingly.
1 | 2024-01-16 |  | JEG | Compressed Air - material, design, specification? Who owns design procurement of the pipe |  |  |  | 1st floor design is TSI?? 1/23: JEG to pusue design and material after approval. 1/30 - Ghafari to submit by Friday 2/6 - 30 additional compressed air drops, 15 per side. 2/13 - ghafari had their 60% review yesterday 2/27 - JEG waiting on pricing. John following up with Ghafari to see if were cleared to proceed with 60% drawing
4 | 2024-01-16 |  | GM | Back stage staircase not getting put in - TSI piping interfere
4 | 2024-01-19 | 2024-01-30 | GM | Wooshin Connection List - Panels R1, R2 and Panel U |  |  |  | Since Hirano manufactured the equipment and disassembled them, Wooshin unable to comprehend accurate data. Wooshin currently not in the cable connection stage. Follow up with Wooshin for update. Repeat Issue
4 | 2024-01-22 | 2024-01-30 | BMC | GAD drawings for Anode and Cathode. Sign off sheets for each piece Drip pans - crate info, layout, ID Equipment Elevations Sequence of Install Assistance in Building material request sheets |  |  | TSI | GAD drawings to be submitted 1/24
4 | 2024-01-23 |  | IICC | Joong Won DCR response to AMS - How to proceed |  |  |  | In process.
4 | 2024-01-23 | 2024-01-30 | BMC | Pit wall Sus Plate layout confirmation. One wall or Two? East or West Wall |  |  | Daejin | BMC to issue DCR. Waiting on approval
4 | 2024-01-23 | 2024-01-30 | Conti E | Cable Duct / Hirano Air Duct interference 2F |  |  | Hirano | DCR submitted
4 | 2024-01-23 | 2024-02-21 | IICC | Pedestrian door access Anode #1 Coater 2F |  |  | BMC | Waiting for Kane to physically mark the size of it 2/7 Kane arrived on site and could not get on the stage
1 | 2024-01-23 |  | IICC | Cathode 2F IPD Duct interference with Hirano duct installation |  |  | Joong Won | Meeting at 1pm to review 2/6 - AMS got up there today to start looking at the situation 2/20 - AMS looking into more detail 2/27 - walking tomorrow with Ultium Main. To finalize the locations
4 | 2024-01-23 | 2024-02-06 | JEG | Expansion loops interfering with building steel - Line 1 |  |  | TBD | JEG to issue DCR 1/23 walk to review.
4 | 2024-01-23 | 2024-01-30 | JEG | Main pipiing pneumatic control valves - who is supplying, when - build sequence? When to install relative to system commissioning. |  |  | TBD | JEG to issue DCR Hirano valve? Install before the pressure test
4 | 2024-01-26 | 2024-02-13 | Conti E | Directed to sleeve all encoder cables in seal tight and pull through cable tray. Recommended to pull through 3/4 and 1 inch seal tight and pull through the raceway |  | 2/2/2024 now 2/13/24 |  | 1/30 - cable tray believed to small. Do we proceed with U2 installation way? Hirano for final say 2/6 - drop dead date will be 2/13 and we proceed with UC2 2/7 - per Jayden : sleeves must be installed for the whole green motor cable 2/13 - directed to sleeve everything
4 | 2024-01-30 | 2024-02-20 | Norris | Roll Leveling - Who is handling the work? |  |  |  | Minkoo - Daejin quoting this work right now 2/26 - Anode, 3/4 Cathode - have to push Cathode 3/18 2/20 - Daejin has the PO for this work. Cathode 1 month after 3/26 start
4 | 2024-01-30 | 2024-02-20 | AMS | Duct work fix on site - Welding. Will submit a financial DCR |  |  |  | 2/6 - line 2 right now is 2/19 60 joints Anode, and 70 in Cathode - AMS to look at this, found 12 additional joints
4 | 2024-02-02 | 2024-02-13 | Conti E | Humidification Units |  |  | ??? | LG has stated not in UC3, Dunham saying still in UT matrix.
3 | 2024-01-23 |  | Conti E | Cable Pull Schedules needed for Coater Corridor equipment. |  |  | TSI | 2/6 - TSI to field check. Conti checked and its not even close 2/20 - TSI is investigating, couple weeks
4 | 2024-02-06 | 2024-02-13 | IICC | Inspection Equipment - Mr. Park cannot find. N-SYS, Glim - BMOU2454560, Cegu4821805
2 | 2024-02-13 |  | Conti E | Remove IPD duct work in Corridor to get Conti Electric panels in |  |  | GM | 2/27 - how to repair duct work, panels set in final place
4 | 2024-02-13 | 2024-02-20 | Conti E | Wooshin cable tray needs to move, TSI to hit sprinkler pipe. Move of 4100mm
4 | 2024-02-13 | 2024-02-27 | Norris | Hoist Steel missing for Line 1 - Now middle of March |  |  | Daejin | Expedite shipping? 2/20 - arrive 3/20. Daejin to get a hoist layout to Norris 2/27 - still waiting on the booths. Layout for hoist and rail received
1 | 2024-02-13 |  | AMS | Centerline and Ductwork is off for Line 2 - same as line 1 |  |  |  | Need to relocate Shambaugh sprinker pipe 2/20 - pending submission later today 2/27 - GM sent information out this morning to Minboo. Need to take another look at it
3 | 2024-02-15 |  | JEG | Joongwon supplied small amount of materials for insulation. RL Bondy needs more material (screws,wire, adhesive) |  |  | Joongwon | 2/20 - received more wire, and working on getting more adhesive. Joongwon is purchasing
1 | 2024-02-19 |  | Conti E | Relocate 13 disconnects on Cathode 1F |  |  | Conti E | 2/20 - Conti working on pricing for this item will be sent to IICC. Conti to mount to column
1 | 2024-02-19 |  | JEG | Piping and blower 2-12 door clash - Cathode 2nd floor |  |  |  | 2/20 - there will be pipe modification for this work. 1 location, supply line 2/27 - Jeg working their way towards this interconnection piping (blower coils)
4 | 2024-02-20 | 2024-02-27 | GM | Damper Locations - Anode 1F, put on backwards |  |  |  | 2/20 - field walk today discuss work
2 | 2024-02-20 |  | Norris | Fire Line interference with the ME booth - Cathode Top stage line 1 |  |  | Daejin | 2/27 - conti waiting to see if there is an interference and will fix at that time if it does
1 | 2024-02-20 |  | Minkoo | Coater Anode - Blower Welding 1/1,1/11,2/1,2/2 |  |  | IICC
1 | 2024-02-20 |  | IICC | Line 2 SUS Plate Ship Date |  | 2024-03-05 | Daejin | 2/27 - currently being manufactured.
2 | 2024-02-27 |  | GM/Conti | Pressure transducer for the blowers |  |  | Daejin
2 | 2024-02-27 |  | GM/IICC | Humidity Sensors - Locations |  |  | Hirano
1 | 2024-02-27 |  | GM/IICC | Curtain Wall - Do we have enough to complete 1 Line |  |  |  | 2/27 - coater length
2 | 2024-02-27 |  | IICC | Roll Filter Anode and Cathode Exhaust - No Panel, is it In or Out |  |  | Ultium (Jang)
2 | 2024-02-27 |  | Conti E | Auto Dampers - In or Out |  |  | Ultium (Jang)
2 | 2024-02-27 |  | Conti E | Cathode Cable Tray Drawing - Top and Back |  |  | Wooshin
2 | 2024-02-27 |  | Conti E | Roll Map Panel Placement |  |  | Minkoo
1 | 2024-02-27 |  | IICC | Install Plan for Outside Fans |  |  | Ultium (Jang)

## SRP
UItium #3 Lansing Battery Plant Process Equipment Installation Project OPEN ISSUE TRACKING MATRIX - SRP
1
2
3
|  | 4 |  |  |  |  | AS OF DATE: | 2024-03-01 08:01
PRIORITY | DATE ADDED | DATE CLOSED | ADDED BY | OPEN ISSUE | RESOLUTION | DUE DATE | RESPONSIBILITY | COMMENTS
3 |  |  | SAIL | Latest FOB dates to be communicated, track weekly for updates / changes. |  | 2023-12-12 | MEC | FOB dates received: Mid October (Absorber, Distallation, Reboiler, Module Skid) Tower Internal: Arrived in Lansing 10/23 Control Panel – ASK: early November requested - expedited, early Jan delivery ROS MEC: Middle December FOB - Early Feb ROS - VEC ok with delivery date. (ROS "Plan" per schedule is 1/1/24) Tank – Mid Dec or Jan - ROS Plan...?. MEC procures locally, Jon to clarify ROS dates with MEC. Absorber 11/1 Baltimore USA - ROS Plan: 11/30 Pumps/Distributor/Vacuum - ship date…? Plan ROS: 12/10/23 Towers on-site Line 1: 12/19 Line 2: 1/29 Craine Schedule - VEC to clarify Modules on-site: 12/11 (how are these being off-loaded?) - arriving tarped, will need to be unwrapped to lift and set. Distillation arrived, stays on truck. Absorbers to re-start 12/27, planned arrival in PM. Absorbers arriving 1/29/24 on site . 2/5 delivery current forecast. Stand purification ahead of next delviery. Continue insulating. 1/30 - possible new shipping way per Matias 2/6 - line 3 & 4 together. We are handling the shipping for the last remaining 5 vessels 2/27 - onsite before county work begins
4 |  | 2024-01-09 | VEC | Documentation requirements, reporting, QC (redlines, leak testing, continuity, etc) |  | 2023-11-06 | IICC | TBC
3 |  |  | LGES | Design comparison for MI2 & UC3 designs for NMP circulation system, include level of insulation and gasket specifications. Ultium to evaluate design change request and specify details of change. |  | 2023-01-05 | MEC IICC / VEC | Comparison data sent by 10/20. Need to know the full range of change Eric to organize an off-line meeting to level set and define next steps. Status / Next Steps…? Follow MI2 piping, insulate all electronic components. Heat Trace (?) NMP & Cooling Water Lines, All the tanks. LG asking for same as MI2. Scope to upgrade UC3 is clear. Quotation needed MEC + Install Team. ~ 2 weeks to quote. Follow up mtg MEC & VEC to clarify. 11/7 - VEC providing pricing next Tuesday for all three options 11/13 - ROM estimates received. Next steps? 12/5: Line LIst to be updated and provided by LG including insulation thickness. Electric panels to be added if needed. 3 weeks to quote. --> Complete 12/11. Targeting 1/5 for Quotation.
2 |  |  | VEC | Isolation Valves recommended for a "phased start up". Addition of four valves required. Approval of change and costs needed. |  | 2023-12-26 | Mark / Kevin | IICC to send request to Minkoo to evaluate - complete DCR 002 sent to GM/LG/UC Add to drawings & prepare a cost estimate for material & install. Quote to be prepared. 11/13 - ROM estimates received. Next steps? Quoted - Need FO approval to proceed.
4 |  | 2024-02-20 | VEC | Laydown area, additional preparation including gravel install needed. |  | 2023-12-12 | GM / Ultium | 10/31 walk planned. Laydown space south of ring road needs to be prepared. BMC communicating "not in scope". Grade it flat, and that is all at this moment. Coordinate through Alan Plan to complete? 11/7 - Don following up with Alan 12/5 - To be complete by 12/4 Latest - Ring Road option likely plan of record. Quote for matting provided by VEC. Feedback needed. East side - latest, further direction from GM/LG
3 |  |  | VEC | Verify Key Dates ("by others"): Power on to SRP bus Nitrogen System Complete Boiler System Complete Plant NMP Feed Line Water supply to SRP area |  | 2023-12-19 | GM: J. MacLean | 12/26 Planning - for discussion: Power on SRP bus: 3/2/24 Nitrogen system: 4/1/24 (Piping readiness by JEG?) NMP needed: 4/15/24 - > 5/15/24 now tentative Boiler System: BMC/JEG planning on 2/22/24. Complete 5/24/24? 1/9/24 - NMP and Nitrogen will get pushed
4 |  | 2024-02-20 | VEC | Confirm NMP need date for system commissioning based on RTSO progress Mixing/Coating |  | 2023-12-15 | GM: J. MacLean | Clarification needed. @ RTSO Date: 6/7 (?) Re-evaluate dates and options for provide NMP ahead of RTSO. 2/6 - before 7/8, nitrogen first week of April
4 |  | 2024-01-16 |  | DI Water Pump accessibility. |  | 2023-12-26 | GM: J. MacLean | Reviewing clearance access for maintenance.
2 | 2024-02-06 |  | Superior | Two extra panels will displace Superior panel - New location needed |  |  | GM: J. MacLean | 2/13 - no updates on BIM 2/20 - leaving open until move
1 | 2024-02-26 |  | IICC | Label standards - using the old labels or making new ones |  |  | GM: J. MacLean | John to speak with parties
1 | 2024-02-27 |  | IICC | Scope gap - define whole scope

## FA
UItium #3 Lansing Battery Plant Process Equipment Installation Project OPEN ISSUE TRACKING MATRIX - FA
1
2
3
|  | 4 |  |  |  |  | AS OF DATE: | 2024-03-01 08:01
PRIORITY | DATE ADDED | DATE CLOSED | ADDED BY | OPEN ISSUE | RESOLUTION | DUE DATE | RESPONSIBILITY | COMMENTS
4 | 2023-11-09 | 2024-01-10 | Conti elec. | Layout of AGV'S Anode and cathode |  | 2023-12-27 | Cowintech | Malyk to follow up with Cowin Tech Need input & coordination from Kiju Still in sourcing at Ultium. No mixing AGV's. in Conti scope. Cowintech equipment, scope of charging to be discussed.
4 | 2023-11-09 | 2024-01-10 | Conti elec. | Layout of AGV's for mixing rooms |  | 2023-12-27 | Cowintech | Malyk to follow up with Cowin Tech Need input & coordination from Kiju Still in sourcing at Ultium. No mixing AGV's. in Conti scope. Cowintech equipment, scope of charging to be discussed. In sourcing through Ultium - no time frame at this moment, much later down the road
3 | 2023-11-09 |  | Conti elec. | Install manuals for All FA equipment |  | 1/3/2024 now 1/17/24 now 2/14/24 | Avaco | Cowin Tech to provide, Malyk to follow up. Send links to Dan Hone FA Meeting 12/13 Stockers received. Conveyors needed. (in process). Complete by 1/3. Conveyors 1 & 2 received. 3 & 4 still needed, and missing duct information in the manual. Jan 17th 1/17/24 - manuals will be uploaded 1/23 for Area 400. Missing Area 100 conveyors 2 & 3 1/24: Cathode Material cannot be used for Anode. Anode Electrical to be delivered mid February. Manuals for 100 & 400 uploaded. Cowin verifying if 100 is correct. Avaco manuals still waiting...1/26 submission planned for Area 200 (Electrical, Mechanical, Drawings and Install Manuals). 1/31 - jumbo roll, rgv, bridge conveyor logistics. RGV upload Feb 3rd 2/7 - have the install manuals, missing some information on the OP panels - Cowintech Avaco - end of Feb for install for manuals 2/14 - Conti to update next meeting - Avaco and Cowintech 2/21 - cowintech manuals uploaded and good Area 100. Area 200 waiting on some from Avaco. Up to the pancake and notch & roll. Jumbo roll 1 & 2, RGV 2/28 - pancake, Nnd end of march 2/28 - manuals will be coming out, bridge conveyor march 8th.
4 | 2024-01-09 |  | ASI | Overall building and conveyor layout with column numbers. |  | 2023-12-27 | Cowintech | Old versoin on CR. 12/22 last update available on CR. ASI to check.
4 |  |  | ASI | Equipment installation drawings needed. Modified drawings sent, not on CR yet. Drawings to be uploaded today. (using the same VDL centerline) |  | 2023-12-27 | Cowintech | Uploaded. ASI to check. Confirm 100% complete. In process - moving forward right now. Cowintech - 2-3 updated drawings still will be completed 1/15 mezz
4 |  | 2024-01-09 | Conti | Electrical panel locations within Area 100 layout to be re-confirmed. |  | 2023-12-27 | Cowintech | Raw material stocker crane panel moved to oppposite side in UC1, UC2. Panel location is correct per Cowintech
4 | 2024-01-10 | 2024-02-06 | ASI | Jumbo Roll Stockers for Area 200 - Descriptive material pull sheet |  | 2024-01-17 | Avaco | All installation manuals from foil to pancake stocker uploaded by 1/26 Avaco to respond in email
4 | 2024-01-10 |  | ASI | ASI - Anchors, and Drill. Ordered through Hilti |  |  | Cowintech
4 | 2024-01-17 | 2024-02-28 | Conti elec. | All Area 100 Electrical Equipment - As early as we can get it |  |  | Cowintech | Anode delivery date (End Feb), Cathode - Mid Feb 8-14. Panels not arriving till march 4-8th. Complete shipping list by 2/8 2/21 - Anode material check. Update packing list to show container number and arrival on site
4 | 2024-01-17 | 2024-02-21 | ASI | Area 200 Epoxy Floor - Holding up Layout |  | 2024-01-24 |  | 4:15 Walk on 1/24 to verify with Kiju, Minkoo, and team. Additonal Epoxy needed + relocation of electrical racks. ASI started on the foil roll. 2/7 - enough work for a month. Need date for completion of epoxy 2/14 - completion by 2/21?
4 | 2024-01-24 | 2024-02-14 | ASI | Anchor bolts replacements, no zinc, move to stainless. |  | 2024-01-24 | Cowintech | ASI to issue DCR w/ costs - Cowintech to purchase.
3 | 2024-01-24 |  | ASI | Chemical anchors likely frozen (out of spec). |  |  | Cowintech | Area 100 - DCR submitted, OEM + Ultium approval to use needed. Cowin tech directs to use and take any future risk of failure. Need to close out DCR formally. 2/7 - few weeks away 2/14 - once we get to lower track that is when we require the chem anchors - arriving 2/21. 2/21 - Area 100 - financial DCR. 2/28 - cowintech wants ASI to purchase the chemical anchors
4 | 2024-01-31 | 2024-02-07 | ASI | Multiple drawings with same drawing number - Avaco states this is how they do business |  |  | Avaco
4 | 2024-01-31 | 2024-02-07 | ASI | Seeing drawings with no description or part number |  |  | Avaco | Avaco will adjust the description
4 | 2024-01-31 | 2024-02-07 | ASI | Drawings call out both a main part and a mirrored part |  |  | Avaco | Avaco will separate the main and mirrored
3 | 2024-01-31 |  | ASI | Shipment trackers need part numbers in description so ASI knows what part number they are pulling |  | 2024-02-07 | Cowintech/Avaco | Cowintech to respond with an email 2/14 - shipment dates for rest of equipment Avaco/Cowintech 2/28 - ASI still needs updates and what has been changed
4 | 2024-01-31 | 2024-02-20 | ASI | 200 Brass datums do not match with Avaco drawings |  | 2024-02-02 | Avaco | Green light to layout foil stocker in Anode only. The wall is not straight according to Avaco 2/7 - moving forward with foil. Avaco uploaded new drawing 2/14 - foil and jumbo 1 on anode cleared to proceed, Cathode?
1 | 2024-01-31 |  | ASI | 200/300 Anchors and epoxy will have the same issue as 100. Need count of anchors from Avaco |  | 2024-02-21 | Avaco | Avaco sending qty to ASI 2/2 2/7 - qty received, ASI to try anchors next 2/14 - Avaco to provide answer by tomorrow morning on wedge anchors 2/21 - avaco supplying all new wedge anchors. Date? 200 Anode - 2/26, and rest in shipping, waiting on ETA 2/28 - received partial orders for both chem and wedge anchors. Arriving March 1st (Penn Tool).
4 | 2024-01-23 | 2024-02-07 | ASI | Sus Plate Layout for Coating Review - Confirm plate layout with FA equipment layout. Modifcations needed to avoid FA? |  |  | Daejin | Kiju to supply FA layout, compare with Daejin plate layout as next step. Minkoo will send update tomorrow 1/24. 1/30 - Kiju answer needed
4 | 2024-02-07 | 2024-02-14 | Conti elec. | Requesting to upload CAD drawing to CR |  |  | Avaco
4 | 2024-02-07 | 2024-02-14 | ASI | Requesting layout for the fence |  |  | Avaco | ASI to review
4 | 2024-02-07 | 2024-02-14 | Conti elec. | CAD drawing rail, duct work, misc. |  | 2024-02-09 | Avaco
4 | 2024-02-13 | 2024-02-14 | GM | Installation Manuals uploaded in Archive folder |  |  | Cowintech
2 | 2024-02-14 |  | ASI/Conti M | Updated Drawings - Mezz, VDLs, Platforms - Area 200 |  |  | Avaco | ASI and cowintech to talk 2/15 2/21 - still need Area 200 conveyor drawing. Avaco uploaded Jan 26th 2/28 - line marking drawing but back to the datums is needed. 200 Jumbo
4 | 2024-02-14 | 2024-02-21 | ASI | Check Sheets & Installation Sheets
2 | 2024-02-14 |  | ASI | Area 300 Drawings |  |  | Avaco | Avaco to discuss with HQ and get date once the final brass datums go in on the 24th. Avaco will need 1 week to finalize drawing 2/28 - drawings in two weeks 3/13, max 3 weeks
2 | 2024-02-14 |  | ASI | Engineer Fix for Anchor Bolts - Only to drill 90mm |  |  | Avaco | Date for the fix? ASI working in the field to remove. Answer by 2/23 2/28 - fix is engineered but no part to complete this work. Arrival march 7th
4 | 2024-02-14 |  | Conti Mechanical | 200 Drawings |  |  | Avaco
2 | 2024-02-14 |  | ASI | Elevators, VDLs - Pancake, Conveyors - On Site Date |  |  | Avaco | Avaco to provide date 3/1
4 | 2024-02-19 | 2024-02-21 | ASI | Avaco 200 drawing request |  |  | Avaco
4 | 2024-02-21 | 2024-02-28 | Conti elec. | Electrical panel locations Area 400 |  |  | EQ Cell | CC-link uploaded to CR as well
2 | 2024-02-28 |  | Conti elec. | Allowed to go off Power Matrix uploaded by EQ Cell on 2/13 - Area 400 |  |  |  | Conti to Submit DCR
1 | 2024-02-28 |  | ASI | Support on the floor - waiting for sign offs, etc. |  |  | Avaco
1 | 2024-02-28 |  | IICC | Updated packing list, and an accurate packing list of anything coming in the future |  |  | Cowintech

## Roll Press
UItium #3 Lansing Battery Plant Process Equipment Installation Project OPEN ISSUE TRACKING MATRIX - Roll Press
1
2
3
|  | 4 |  |  |  |  | AS OF DATE: | 2024-03-01 08:01
PRIORITY | DATE ADDED | DATE CLOSED | ADDED BY | OPEN ISSUE | RESOLUTION | DUE DATE | RESPONSIBILITY | COMMENTS
4 | 2024-02-15 | 2024-02-29 | Team | Drawings Needed by March 1st |  |  | CIS/LG
4 | 2024-02-15 | 2024-02-29 | IICC | Grouting Specs - CIS bringing material |  |  | IICC
1 | 2024-02-15 |  | Conti E | Panel Schedule - 6-8 Week Lead Time |  |  | Dunham
1 | 2024-02-15 |  | Conti E | ME Booths - calling for 100amp single breaker |  |  | Dunham/Superior | Conti to submit DCR in regards to both open issues for Dunham
4 | 2024-01-09 | 2024-02-29 | Conti E | Roll Press - conti would like to start pull ahead. Release of equipment schedules
2 | 2024-01-29 |  | Conti E | 24 Additional Oil Heaters - Per the IFR |  |  |  | 2/13 - Roll press cathode, figure out lines 3 & 4 later. Complete lines 1 & 2 2/22 - additional information on the 2/27
2 | 2024-02-22 |  | Conti E | Tray Layout |  |  | CIS | 2/29 - Conti has requested layout from CIS, information provided to Jay Chul and John Maclean
1 | 2024-02-28 |  | Superior | Cable Specs
2 | 2024-02-29 |  | Conti M | UT for Hookups - Chilled Water: No pipe size |  |  | CIS
2 | 2024-02-29 |  | Conti M | Flow Meter and Thermostat - Will adjust drops, need location for both items |  |  | CIS
2 | 2024-02-29 |  | IICC | Spider Boxes in Roll Press | C
2 | 2024-02-29 |  | IICC | CIS Trailer Power

## Area 400 (hidden)
UItium #3 Lansing Battery Plant Process Equipment Installation Project OPEN ISSUE TRACKING MATRIX - AREA 400
1
2
3
|  | 4 |  |  |  |  | AS OF DATE: | 2024-03-01 08:01
PRIORITY | DATE ADDED | DATE CLOSED | ADDED BY | OPEN ISSUE | RESOLUTION | DUE DATE | RESPONSIBILITY | COMMENTS

## Area 500 (hidden)
UItium #3 Lansing Battery Plant Process Equipment Installation Project OPEN ISSUE TRACKING MATRIX - AREA 500
1
2
3
|  | 4 |  |  |  |  | AS OF DATE: | 2024-03-01 08:01
PRIORITY | DATE ADDED | DATE CLOSED | ADDED BY | OPEN ISSUE | RESOLUTION | DUE DATE | RESPONSIBILITY | COMMENTS

## Miscellaneous (hidden)
UItium #3 Lansing Battery Plant Process Equipment Installation Project OPEN ISSUE TRACKING MATRIX - Miscellaneous
1
2
3
|  | 4 |  |  |  |  | AS OF DATE: | 2024-03-01 08:01
PRIORITY | DATE ADDED | DATE CLOSED | ADDED BY | OPEN ISSUE | RESOLUTION | DUE DATE | RESPONSIBILITY | COMMENTS